## Slide 1
AI in Power Plants
From Data to Decisions
An introduction to Artificial Intelligence for smarter plant operation and maintenance
PREDICT · DIAGNOSE · OPTIMISE · ASSIST
MAHAGENCO Training Centre, Nashik
Full-day programme · 10:00–13:00 and 14:30–17:00 · in person at Nashik, with participants online from Koradi, Khaperkheda, Bhusawal and Paras
PRESENTER
S. H. Parihar
Power sector engineer · author · AI practitioner
AUTHOR OF
Lean AI
Learn the English that AI Understands
AI for Busy Parents
16 years
experience in the power sector
Notes: [Slide 1 · Opening · target 0:00] [10:00–10:02] Welcome everyone, including the stations joining online. Set the tone in the first thirty seconds: this is not a computer science lecture, and nothing today is theoretical. Every example uses equipment you have walked past this week, and after lunch we will work entirely from MAHAGENCO's own June 2026 numbers. Say plainly: 'I am not here to tell you AI will run your plant. I am here to show you what it can do with data you already have, what it cannot do, and how to pick one sensible thing to try at your station.' Housekeeping: ask everyone to open the simulation lab file on their laptop now, before the first break, so nobody is fighting with a file transfer at 11:41. Confirm the online stations can see the slides and hear clearly, and ask them to use chat for questions.

## Slide 2
What you will take away
Session objective — one working day, four things you keep
Opening
2
1
A working mental model of AI
What machine learning, generative AI and an agent actually are, described in plant language rather than in vendor language.
2
Where it earns its keep in a power station
Availability, heat rate, auxiliary power, coal quality and knowledge — the places where a thermal station has real money on the table.
3
An honest view of the limits
What AI gets wrong, where it must never be connected, and why most programmes fail for reasons that have nothing to do with the algorithm.
4
A first step you can take at your own station
One pilot, chosen from your own June 2026 numbers, that a named engineer can run in ninety days without a fleet-wide sanction.
Notes: [Slide 2 · Opening · target 10:00] [10:00–10:03] Open on time and open on the objective, not on yourself. Three minutes, no more. Line to say: 'By five o'clock today you will not be a data scientist, and that is not the aim. You will be an engineer who can tell a real AI opportunity from a slide deck.' Walk the four rows quickly and spend your time on rows three and four. This room has sat through vendor presentations before, and the fastest way to lose it is to oversell in the first minute. Say plainly that we will spend as much of today on what AI gets wrong as on what it does well. Row four is the one to land. Every station represented here has its own June 2026 numbers, and by the last session each of you will have picked one pilot from your own evidence, with a named owner and a ninety-day plan. Ask the room to hold one question in mind all day: which machine at my station has hurt me twice in the last two years? We come back to that question at five o'clock.

## Slide 3
The day, hour by hour
Nine sessions, two tea breaks and lunch — with the simulation lab running through the middle of it
Opening
3
1
AI fundamentals
10:10–11:10
·
Tea
11:10–11:25
2
Intelligent monitoring
11:25–12:10
3
Predictive maintenance
12:10–13:00
·
Lunch
13:00–14:30
4
Reading our own numbers
14:30–15:00
5
What other generators have done
15:00–15:12
6
Performance optimisation
15:12–15:45
·
Tea
15:45–15:55
7
Generative AI, RAG and agents
15:55–16:28
8
Computer vision and emerging
16:28–16:40
9
Implementing responsibly
16:40–17:00
8 hands-on
simulation modules that run offline, in a browser, on the laptop in front of you
Breaks
Morning tea
11:10 – 11:25
Lunch
13:00 – 14:30
Afternoon tea
15:45 – 15:55
Notes: [Slide 3 · Opening · target 10:03] [10:03–10:06] Show the shape of the day rather than reading it out. Point at the three places the labs sit — Sessions 2, 4 and 6, and again in Session 7 — and tell everyone to open the simulation lab file now so nobody is fighting a file transfer at 11:41. Flag Session 5 specifically: twelve minutes on what other generators have actually achieved, with published numbers. It sits deliberately straight after we look at our own figures. For the online stations, say when the breaks are so they can plan around them, and name the three checkpoints where you will hand over to them for questions.

## Slide 4
How today works — the simulation lab
Eight modules you run yourself, and one boundary that applies to all of them
Opening
4
One file, no internet
A single HTML file that opens in any browser on your own laptop. No installation, no login, no network. It works with the cable unplugged.
Real algorithms, stated data
Nearest-neighbour residuals, ridge regression, TF-IDF retrieval — genuine code, not animation. Data is either our actual June 2026 figures or synthetic data whose physics equations are printed on screen.
You keep the file
Copy it to a pen drive and take it away. Re-run every module at your own station, with your own people, whenever you want.
A teaching instrument, not a plant model
These modules are not calibrated to your unit. Nothing that appears on these screens today should ever influence an operating decision.
Real algorithms, honest data, no plant authority. Learn the method here, and validate every result against your own engineering before it means anything.
Notes: [Slide 4 · Opening · target 10:06] [10:06–10:10] Four minutes on the lab, and be precise, because credibility for the whole day rests on this slide. Card one: one HTML file, opens in any browser, no internet, no installation, no login. Ask them to open it now and confirm that it loads before we start session one. Card two is the one that matters to an engineer. The algorithms are real — a nearest-neighbour residual model, a ridge regression trained live by gradient descent, a TF-IDF retrieval index. Nothing is animated. Where the data is our own June 2026 figures it says so on the screen; where it is synthetic, the physics equations that generated it are printed alongside. Card three: the file is theirs. Take it to the station and run it again with their own team. Card four is the caution, and it must be said clearly rather than softened. These are teaching instruments. They are not calibrated models of anybody's unit. Nothing produced here should influence an operating decision. Ask directly whether that boundary is clear, and get a nod before moving on.

## Slide 5
1
SESSION
AI fundamentals for power plant engineers
What AI, machine learning and generative AI actually are — in plant language, not vendor language
The one idea that matters: expected versus actual
How a machine learns from plant data, and how it is used
Inside a neural network, without the mathematics
How to judge a model the way an operator will
What AI is not — and the data pathologies that break it
10:10 – 11:10
60 minutes
5
Notes: [Slide 5 · 1. AI fundamentals · target 10:10] [10:10] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 6
What AI actually is
Four words vendors use interchangeably, and why the difference matters to you
1. AI fundamentals
6
AI
ML
DL
Artificial Intelligence
Any technique that makes a machine do something we would call intelligent. Rule-based expert systems count. The interlock logic in your DCS is, strictly, the oldest form of it.
Machine Learning
The machine works the rule out from data instead of being handed it. Almost every application in today's course sits inside this ring.
Deep Learning
Machine learning using large neural networks. Needed for images, sound and language. Usually overkill for process signals out of a historian.
Generative AI
Beside the circles, not inside them. Models that produce new text, images or code. Excellent with manuals, SOPs and reports. Knows nothing about your unit until you give it your documents.
Notes: [Slide 6 · 1. AI fundamentals · target 10:10] [10:10–10:14] Keep this crisp — four minutes maximum. The room does not need taxonomy, it needs to stop being confused by vendor vocabulary. Line to say aloud: 'The interlock logic in your DCS is, strictly speaking, artificial intelligence. Somebody wrote the rule. Machine learning differs in exactly one respect — the machine works the rule out from history instead of being handed it. That is the entire idea, and everything today sits on top of it.' Point at the middle ring and say that almost everything of value in a thermal station today lives there, not in deep learning. On the aside: 'Notice generative AI is beside the circles, not inside them. Different tool, different job — documents and language, not process signals. People conflate the two constantly and then wonder why a chatbot cannot predict a bearing failure.' Ask the room how many have sat through a vendor presentation using all four words interchangeably. Hands will go up. Tell them that by the end of this hour they will be able to ask the one question that sorts a real system from a slide.

## Slide 7
The asset you already own
What a 210 to 660 MW unit holds today, with no new investment at all
1. AI fundamentals
7
Source | What it holds | Typical volume (indicative) | What it is used for today
DCS and historian | Pressures, temperatures, flows, MW, damper and valve positions | Thousands of tags per unit | Live screens and trends
Vibration and condition monitoring | Shaft and bearing vibration, orbits, spectra | Continuous on TG, route-based elsewhere | Alarm and periodic review
CMMS / SAP PM | Work orders, defect history, spares, notifications | Years of records per station | Compliance reporting
Chemistry lab / LIMS | Cycle chemistry, coal and ash analysis | Daily to hourly | Statutory records
CEMS | Stack emissions and opacity | Continuous | Regulatory submission
Coal and fuel accounting | Rake weights, loading and unloading GCV, transit loss | Every rake, every day | Bill preparation
Documents | Manuals, SOPs, RCA and trip reports, drawings | Decades of paper and PDF | Found when someone remembers it exists
4,588 MU
sent out in June 2026 — recorded second by second, and almost none of it ever re-read
Notes: [Slide 7 · 1. AI fundamentals · target 10:14] [10:14–10:18] This slide has one job: nobody has to buy anything to start. Read the last column aloud, slowly — 'live screens and trends', 'compliance reporting', 'statutory records', 'bill preparation', 'found when someone remembers it exists'. That column is the problem statement for the whole day. Be honest about the volumes: they are indicative, not audited. Ask the room instead — 'roughly how many tags does your unit historise, and when did anyone last analyse a full month of them?' The stat card is verified. 4,588 MU sent out from the thermal fleet in June 2026, billed at ₹2,806.55 crore. Every unit of that was measured, timestamped and stored. Then say the uncomfortable part: almost none of that record was re-read after the shift in which it was created. Land the point. The constraint is not data collection — we are excellent at collecting. The constraint is that the data is stored for compliance and never interrogated for decisions. That is what changes today.

## Slide 8
The one idea that matters
Expected versus actual — the residual
1. AI fundamentals
8
THE QUESTION A FIXED ALARM ASKS
Is it above 90 °C?
One tag, one number, no context. The same 90 °C setpoint at 55 per cent load on a January night and at full load on a May afternoon. It cannot tell the difference, and it was never asked to.
THE QUESTION A MODEL ASKS
Is it above what it should be?
Given this load, this ambient, this cooling water inlet and this oil flow, the model says what the bearing should read right now. Subtract that from what it does read. What is left over is the only part that carries information about the machine.
Actual minus expected is the residual. Every process-data application in this course is built on that one subtraction — and Session 2 walks a real bearing through it week by week.
Notes: [Slide 8 · 1. AI fundamentals · target 10:18] [10:18–10:23] Slow right down. This is the single most important slide of the day. If they remember nothing else, they must remember expected versus actual. Use a bearing everyone knows — an ID fan or a BFP bearing. Say: 'Seventy-four degrees means nothing on its own. Seventy-four at fifty-five per cent load on a January night is a problem. Seventy-four at full load in May is completely normal. Your fixed alarm cannot tell the difference and was never designed to. A model can, because it has seen thousands of hours of what normal looks like at every load and every ambient.' DO NOT give the week-by-week numbers here. Slide 26 walks the whole degradation through and the five weeks of warning is its reveal. Spend it now and that slide has nothing left to deliver. Set up the idea; let Session 2 pay it off. Finish on the subtraction and move on. If the room is with you on this one line, everything after lunch lands.

## Slide 9
How a machine learns from plant data
The same four steps sit behind almost every application you will see today
1. AI fundamentals
9
1
Learn normal
Feed the model a period of genuinely healthy running — ideally a full year, covering the whole load range, summer and winter, and every coal blend you actually fire.
2
Predict expected
For every minute, the model estimates what each signal should be, given every other signal. Not a physics equation — a pattern learned from thousands of hours of history.
3
Compute the residual
Actual minus expected, signal by signal. Small and noisy when the machine is healthy, because load and ambient conditions have already been accounted for.
4
Flag persistence
A residual that grows and stays is a developing fault. A single spike is a sensor or a transient. Persistence logic is what makes the alert believable.
Step one decides everything. Train on a period that already contained the fault and the model learns the fault as normal.
Notes: [Slide 9 · 1. AI fundamentals · target 10:23] [10:23–10:27] Walk the four boxes at a steady pace. This is the mechanism behind everything for the rest of the day. Hammer step one. 'Genuinely healthy running' is where most failed projects die: the training period already contained the developing fault, so the model learned the fault as normal and never raised anything. You will watch exactly this happen in the lab before lunch, on your own screen. Step two deserves a sentence of reassurance. No physics equation is written. Nobody derives a heat balance. The model learns the relationship between signals from history alone. Step four is what keeps the system switched on. Say it plainly: 'A spike is a sensor. A slope is a machine. Any system that alerts on spikes will be switched off within a month, and rightly so.' Close on the punch line and add the framing that keeps the room on side all day — the model produces a number, the engineer decides what it means.

## Slide 10
How a model is built, and then used
Two separate pipelines that people constantly confuse — training happens once, inference happens every minute
1. AI fundamentals
10
TRAINING — once, offline, with an engineer curating
Historian export
12 months of tags
Clean and align
gaps, freezes, timestamps
Build features
normalise for load and ambient
Split by time
train on early, test on late
Fit the model
minimise error on training data
Test honestly
on data it has never seen
INFERENCE — continuously, online, unattended
Live tag values
every minute
Same feature recipe
identical to training
Frozen model
no learning at run time
Expected value
what it should read
Residual + persistence
actual minus expected
Engineer decides
advisory, never automatic
Feedback: Retrain when the machine changes: after an overhaul, a retrofit, or a change of coal source
Notes: [Slide 10 · 1. AI fundamentals · target 10:26] [10:26–10:30] Draw the two lanes apart deliberately. The most common misunderstanding in the room will be that the model 'keeps learning' while it runs. It does not, and it must not — a model that learns continuously will quietly learn a developing fault as normal. Walk the top lane left to right. Stop at 'Split by time' and say why random splitting is wrong for plant data: shuffle a time series and the model sees tomorrow while training on today, and the test result becomes a lie. Walk the bottom lane. Stress 'Same feature recipe' — if the training pipeline normalised by load and the live pipeline does not, everything downstream is wrong, and this is one of the most common deployment defects. End on the feedback arrow. Ask: 'Who at your station would know that a mill was re-lined last Tuesday?' That person is part of the AI system, whether or not anybody has told them.

## Slide 11
Three ways machines learn
Two plant examples each — and where the value actually sits for us
1. AI fundamentals
11
Family | What it needs | Plant example 1 | Plant example 2
Supervised — learns from labelled examples | History where you already know the answer | As-fired GCV predicted from plant signals, with lab results as the answer key | Vibration signature classified as unbalance, misalignment or looseness
Unsupervised — finds structure with no labels | Only a clean period of healthy running | ID fan or mill anomaly detection, with no failure history at all | Grouping operating states to spot an unusual mill combination
Reinforcement — learns by trial and consequence | A simulator, or a very tolerant process | Combustion setpoint search, in a simulator only | Not appropriate for direct control of a utility boiler today
Most plant value today comes from the middle row. It needs no failure history — only one clean period of healthy running.
Notes: [Slide 11 · 1. AI fundamentals · target 10:27] [10:27–10:31] Three families, two plant examples each. Four minutes, no more. The key teaching point is the punch line, and it answers the objection that always comes: 'but we have no failure data.' The answer is that the most useful family for a power station needs none. Unsupervised anomaly detection needs one clean year of healthy running and nothing else. On supervised learning, use the GCV example — the lab result is the answer key, and your station already generates it every day. That is a soft sensor, and it is SIM-4 this afternoon. On reinforcement learning be blunt and be early: 'You will hear a great deal about this. It is real, it is impressive in simulation, and it is not ready to be let loose on a utility boiler. Anyone telling you otherwise is selling.' Ask the room which of the two unsupervised examples they would start with on their own unit. It gets them thinking in terms of candidate applications rather than technology.

## Slide 12
A tag is not a feature
Why raw historian values go into a model badly, and what engineering fixes them
1. AI fundamentals
12
Raw tag, as the historian stores it
Bearing temperature, 74 °C — meaningless without load and ambient
Mill current, 62 A — depends entirely on coal flow and fineness
Condenser back pressure — moves with CW inlet temperature all year
APH outlet gas temperature — moves with load, coal and air flow
One instantaneous value, with no memory of the last six hours
The feature an engineer builds from it
Temperature rise above cooling medium, normalised for load and ambient
Current per tonne of coal — a ratio that holds across the load range
Back pressure minus achievable at today's CW inlet — the controllable part
Gas-side and air-side differential, and the leakage ratio derived from it
Rolling mean, standard deviation and slope over one, six and twenty-four hours
Feature engineering is where plant knowledge enters the model. It is the one part a data scientist cannot do without you.
Notes: [Slide 12 · 1. AI fundamentals · target 10:31] [10:31–10:35] This is the slide that shows engineers exactly where they are indispensable. Read one pair across, left to right — bearing temperature at 74 °C on the left, temperature rise above cooling medium normalised for load and ambient on the right. Then say: 'The left column is what your historian stores. The right column is what a model can actually learn from. Turning one into the other is called feature engineering, and it is the single highest-value contribution an experienced engineer makes to an AI project.' Make the ratio point concrete. Mill current on its own tells you nothing. Mill current per tonne of coal holds across the whole load range and rises steadily as the grinding elements wear. Make the memory point too. One instantaneous value has no history. Rate of change over ten minutes, and rolling statistics over one, six and twenty-four hours, are what allow a model to see a trend rather than a reading. Land the punch: this is where your plant knowledge enters the model, and it is not optional.

## Slide 13
Inside a neural network, without the mathematics
What is actually happening between the inputs you know and the output you want
1. AI fundamentals
13
Inputs
Plant tags: load, O₂, mill combination, burner tilt, coal GCV, ambient
Hidden layer 1
Each node forms a weighted combination of the inputs, then applies a simple non-linear bend
Hidden layer 2
Combinations of combinations — this is where interactions between variables get represented
Outputs
NOx, unburnt carbon, heat rate
What is actually happening
A 'weight' is just a multiplier the machine adjusts. Training means nudging every weight, thousands of times, until the predicted outputs match history.
The non-linear bend at each node is what lets the network represent a curve rather than a straight line. Without it the whole network collapses to simple linear regression.
Nothing inside is a physical quantity. The hidden nodes do not correspond to anything you can point at in the boiler — which is exactly why explainability tools matter.
For most plant process data a network this small is enough. Deep networks with millions of weights are for images, sound and language, not for forty tags.
A neural network is a very flexible curve fitted to your history. Its power and its danger are the same thing: it will fit anything you give it, including nonsense.
Notes: [Slide 13 · 1. AI fundamentals · target 10:34] [10:34–10:38] Draw attention to the fact that there is no physics in the diagram. The network has no idea what a mill is. It has learned a shape from your history. The useful analogy for this room: it is curve fitting, with a great many more knobs than a spreadsheet trendline. A polynomial fit has three or four coefficients; this has a few hundred. That is the whole difference in kind. Stress the third note. Because the hidden nodes mean nothing physical, you cannot read the model to understand the boiler. You can only ask it what it would predict, and use tools like SHAP to ask which inputs drove a particular answer. The punch line is the warning. Ask the room: 'If I gave this network the date and the shift-in-charge's name as inputs, would it find a pattern?' It absolutely would, and that pattern would be meaningless. Feature selection is engineering judgement, not a setting.

## Slide 14
Training, validation, and the cardinal sin
How you know a model works before you ask an operator to trust it
1. AI fundamentals
14
Training data
The period the model learns from. Known-good running, wide enough to cover every load, season and fuel the unit actually sees.
Validation data
A period the model has never seen. If it performs here it has learned the machine. If not, it has memorised the training set.
The cardinal sin
Judging a model on data it was trained on. It will look magnificent and fail in week one. Almost every inflated vendor claim starts here.
Time-based split, never random
Plant data is correlated minute to minute. A random split leaks the future into the past. Train January to September, test October onwards.
Ask any vendor one question: what period was the model tested on, and had it seen that period before?
Notes: [Slide 14 · 1. AI fundamentals · target 10:35] [10:35–10:39] Four cards, four minutes. This is how they should judge every vendor claim they meet for the rest of their careers. Take the cardinal sin card slowly. 'Judging a model on data it was trained on is like marking your own examination paper with the answers in front of you. The model will look magnificent. It will fail in the first week of live running.' Almost every inflated performance figure in this industry comes from precisely that mistake. The time-based split card needs the plant analogy. Plant data is correlated minute to minute — split it randomly and the minute before and the minute after a held-out sample are both in the training set, so the model has effectively been shown the answer. Train on January to September and test on October onwards. That is the only honest split for a time series. Give them the question on the punch line and ask them to write it down: 'What period was the model tested on, and had it seen that period before?' The good vendors answer immediately.

## Slide 15
Overfitting, explained physically
The difference between a model that learned the machine and one that learned last year
1. AI fundamentals
15
A MODEL THAT MEMORISED
It learned last year's noise
It reproduces the training period almost perfectly, including the transmitter drift, the odd monsoon fortnight and the month one mill was out. Show it this year and it flags normal running as abnormal, while missing the real drift entirely.
A MODEL THAT GENERALISED
It learned how the machine behaves
Slightly worse on the training period, and far better on data it has never seen. It survives a coal change, an overhaul and a season it was not trained on, because it learned the relationship rather than the record.
A model that fits history perfectly has learned history, not the machine. Suspicion, not admiration, is the correct response.
Notes: [Slide 15 · 1. AI fundamentals · target 10:39] [10:39–10:42] Three minutes. This is overfitting explained without a single equation. Say it physically: 'Imagine a model that has memorised last year perfectly — including the week the transmitter drifted, the monsoon fortnight when CW temperature was odd, and the month Mill C was out. It reproduces all of it beautifully. Now show it this year. It flags perfectly normal running as abnormal, because this year is not last year. And it misses the real drift, because the real drift does not look like anything it memorised.' The counterintuitive line is the one to land: 'A model that fits history perfectly has learned history, not the machine. When a vendor shows you a near-perfect fit, the correct response is suspicion, not admiration.' Ask the room: 'Would you trust an engineer who could recite last year's log book word for word but could not tell you what the unit will do tomorrow?' That is the difference between memorising and generalising, and it is exactly the same distinction here.

## Slide 16
Judging a model the way an operator will
The metric on the vendor's slide is not the metric that decides whether it survives
1. AI fundamentals
16
What the data scientist reports
What the shift engineer actually asks
R² of 0.98 on the test set
How many weeks of warning did it give?
Root mean square error in degrees
How many false alarms will I chase in a month?
Model accuracy of 94 per cent
When it fires, is there something to go and look at?
Area under the curve
Does it tell me which signal moved, and why?
Trained on two years of data
Is it still right after the overhaul?
A very good model nobody acts on
A merely adequate model that changed a decision
Lead time, false alarms per model-month, actionability. Those three decide adoption. R² decides nothing at all.
Notes: [Slide 16 · 1. AI fundamentals · target 10:42] [10:42–10:46] The whole slide is the last row, so build towards it. Go down the left column first and let the jargon sound as alien as it genuinely is. Then read the right column — these are the six questions a shift engineer actually asks, and not one of them appears on a vendor slide. Take false alarms per model-month seriously and define it precisely: one model, watching one machine, for one month. If that produces more than roughly one alert with nothing to find, the engineer will stop opening them. Not from laziness — from arithmetic. Multiply it across two hundred models and the programme collapses under its own noise. Read the last row aloud twice: 'A very good model nobody acts on, against a merely adequate model that changed a decision.' The second is worth more. Always. Ask the room what would make them personally open an alert on a Monday morning. The answer will be lead time, evidence and a next step. That is the specification, and it came from them rather than from you.

## Slide 17
What confidence means, and what it does not
A number without an error bar is an opinion with a decimal point
1. AI fundamentals
17
Confidence is a range, not a promise
A useful output says the bearing should be 68 °C plus or minus 1.5 °C. The range carries as much information as the number.
Two very different uncertainties
The model is unsure because the data is noisy, or because it has never seen this operating point before. The second is far more dangerous.
Calibration
If a model says ninety per cent confident on a hundred occasions, roughly ninety should turn out right. Untested, that percentage means nothing.
Outside the training envelope
At a load, ambient or coal the model never saw, it will still produce an answer. It will be confident, and it will be wrong.
Confidence is not correctness
A generative model will state an invented clearance value with complete assurance. Assurance and accuracy are entirely unrelated quantities.
What to demand
Ask for the error band, the coverage of the training data, and the operating range where the vendor will not stand behind the output.
Any output arriving without an uncertainty attached is an opinion, however many decimal places it happens to carry.
Notes: [Slide 17 · 1. AI fundamentals · target 10:46] [10:46–10:49] Three minutes, six cards. Do not read them all — pick three and let the handout carry the rest. The two-uncertainties card is the one that matters. 'The model is unsure because the data is noisy is a manageable problem. The model is unsure because it has never seen this operating point before is a dangerous one — and most systems present the two identically.' The outside-the-envelope card is the practical one. Say: 'At a load, an ambient or a coal blend the model never saw in training, it will still give you a number. It will give it confidently. And it will be wrong. Ask every vendor for the operating range their model was trained across, in writing.' Land the subtitle as the line of the slide: a number without an error bar is an opinion with a decimal point. Ask them: 'When a vendor quotes 94 per cent accuracy — accuracy at what, over what period, and how wrong is it when it is wrong?' Watch how few can answer the third part.

## Slide 18
Explainability — an alert with its reasons attached
No engineer acts on a number with no justification, and they are right not to
1. AI fundamentals
18
Koradi Unit 9 · BFP 6B · Advisory · 06:40
Signal
Bearing 2 temperature, drive end
Deviation
68.4 °C measured against 64.9 °C expected — plus 3.5 °C
Persistence
Above threshold continuously for 9 days
Largest contributor
Thrust bearing temperature rise per unit of fan power — 61 % of the deviation
Second contributor
Lube oil outlet temperature, rising alongside it — 22 %
Recommended action
Check oil condition and cooler performance at next opportunity — not an emergency
The contribution breakdown is what converts an alert into a work order. Without it you are asking an engineer to trust a number.
Notes: [Slide 18 · 1. AI fundamentals · target 10:49] [10:49–10:53] This is what an alert must look like before an engineer will act on it. Walk the rows in order: the signal, the deviation with both numbers shown, how long it has persisted, then the two contributors with a percentage against each. That contribution breakdown is what the industry calls SHAP-style attribution. In plain terms, the model is asked how much of the total deviation each input explains, and it answers with a number. The line to say aloud: 'No engineer will act on a score of 0.87. Every engineer will act on — bearing 2 is six degrees above expected, it has been for nine days, and most of it is showing up as temperature rise per unit of fan power.' Note what is deliberately absent. No model accuracy, no network diagram, no confidence percentage floating on its own. The operator does not care about any of it. They care what moved, by how much, since when, and what to do about it. Ask the room: would you raise an inspection on this? Usually yes — and that is the test every alert has to pass.

## Slide 19
Where AI genuinely helps in a plant, ranked
An honest view — buy the top, pilot the middle, only read about the bottom
1. AI fundamentals
19
Anomaly detection on rotating plant
Model of healthy behaviour, residual on every signal, persistence logic before any alert is raised
Proven — the safest place to start
Soft sensing
Predicts a value you cannot measure online from values you can, trained on lab results
Proven — needs honest error reporting
Diagnostics
Points at which signals drove the deviation and matches the pattern to known signatures
Emerging — good at pointing, weak at naming
Prognostics and remaining life
Fits a degradation curve to the residual and projects a date with an uncertainty band
Emerging — the band is usually wide
Advisory optimisation
Searches setpoint and equipment combinations, recommends, and leaves the operator to decide
Proven as advisory — gain depends on current tuning
Closed-loop control
Writes bounded bias values to the DCS under clamps, rate limits and a watchdog
Emerging — only with full engineering controls
Vision and language
Cameras reading leaks, gauges and safety; retrieval over manuals, SOPs and trip reports
Proven for document search · Emerging for vision
Start where the answer is a number an engineer can check. Anomaly detection and soft sensing repay their cost before anything else does.
Notes: [Slide 19 · 1. AI fundamentals · target 10:53] [10:53–10:57] Give them a filter they can apply to every vendor presentation they attend after today. That is the purpose of this slide. Work down the rows and stress that the ranking is by where value is genuinely realised in a thermal station, not by how interesting the technology is. Anomaly detection is first because it needs no failure history, touches no control system, and produces a number an engineer can check by walking to the machine. On closed-loop control be careful and precise: 'It exists, it works, and it belongs to a station that already has clamps, rate limits, a watchdog and bumpless transfer engineered. It is not a first project.' On vision and language, split it honestly. Retrieval over your own manuals and trip reports is proven and cheap. Camera analytics is real but needs cameras, lighting and somebody to maintain them. The punch is the takeaway. Start where the answer is a number an engineer can check — which is also the cheapest place to fail safely, and that matters more than it sounds.

## Slide 20
What AI is not
Say all five of these out loud before anyone in this company buys anything
1. AI fundamentals
20
Never in protections
Advisory and statistical, sitting above your interlocks — never inside them. No model output belongs in a trip circuit or a safety function. Not now, not in five years.
Not a judgement engine
It produces a number and a reason. Weighing risk, reading the plant, and deciding what to do on a running unit remain entirely the engineer's work.
Not magic without data
No historised tag, no model. A frozen transmitter, an over-compressed trend or a tag that was never recorded cannot be rescued by any algorithm.
Not a one-time project
A model is a maintained asset. After an overhaul, a retrofit or a sustained coal change it must be retrained, or it will quietly become wrong.
Not a headcount saving
It covers equipment nobody has time to walk round, and gives earlier warning. It does not remove the engineer who decides what that warning means.
Never use a model for: protection settings · trip and interlock logic · permit and clearance decisions · statutory returns without verification · anything reaching the plant without an engineer's signature
Notes: [Slide 20 · 1. AI fundamentals · target 10:57] [10:57–11:00] Read the band at the bottom slowly and deliberately. In a room of O&M engineers this is the slide that decides whether they trust the rest of the day. Say the first one without hedging: 'Nothing in this course goes into a protection scheme, a trip circuit or an interlock. Not now, not in five years. Those systems are deterministic and safety-rated for a reason, and a statistical model has no business inside them.' The one-time project card is the one people underestimate. A model is a maintained asset, exactly like a protection setting. After an overhaul, a retrofit or a sustained change in coal, it must be retrained or it will quietly become wrong while still producing confident output. The headcount card matters for the room's own comfort, so say it directly: 'This covers equipment nobody has time to walk round and it gives earlier warning. It does not remove the engineer who decides what the warning means. That decision is not automatable, and nobody in this room should let it become so.'

## Slide 21
The vocabulary you will hear this year
Eleven words grouped — plain meaning, plant example, and what to watch for
1. AI fundamentals
21
Terms | Plain meaning | Plant example | Watch out for
Model · Training | A rule learned from history, and the act of learning it | One model per ID fan, trained on a year of healthy running | A model trained on a faulty period learns the fault as normal
Feature · Label · Residual | The input you build · the answer you teach · actual minus expected | Load-normalised bearing rise · lab GCV · six unexplained degrees | No label means no supervised model — establish that on day one
Drift · Inference · Edge | The plant moves away from the model · running it · running it near the machine | Model stale after overhaul · a residual every minute · a box in the LT room | Nobody owns retraining after an overhaul
LLM · RAG · Agent | Language model · the same model grounded in your documents · one that calls tools | Draft a trip report · answer from the O&M manual with a citation · assemble a work order | Ungrounded answers invent numbers; an agent needs an approval gate
If a vendor uses a word you cannot map onto this table, ask them to map it. The good ones manage it in one sentence.
Notes: [Slide 21 · 1. AI fundamentals · target 11:00] [11:00–11:04] Eleven words grouped into four rows so they fit on a projected slide. The full glossary is in the handout — tell them that, and do not read the table out. Do land three of them properly. Residual — actual minus expected, and by now they should be able to define it themselves, so ask them to. Drift — the plant moves away from the model, which is exactly why the last column says nobody owns retraining after an overhaul. Grounding, in the last row — an ungrounded language model will invent a clearance value with complete confidence, while a grounded one answers from your own document with a citation you can open and check. The watch-out column is the useful one. Read it down on its own: a model trained on a faulty period learns the fault as normal; no label means no supervised model; nobody owns retraining; ungrounded answers invent numbers. Give them the punch as a working tool for every vendor meeting from next week onwards.

## Slide 22
The data pathologies that quietly destroy models
None of these show up on an operator screen. Every one shows up in the model.
1. AI fundamentals
22
What is wrong with the data
Historian compression and exception deviation set for screen trends, not analysis
A frozen transmitter reading a perfectly plausible constant value
Tags on the DCS graphic that were never configured to historise at all
DCS tag name, historian point and SAP equipment number that do not agree
Timestamps from clocks never synchronised across DCS, historian and lab
Coal and chemistry results living in spreadsheets outside any system
What it does to the model
The slow drift the model exists to catch is discarded before it is ever stored
The residual goes to zero, and the model reports perfect health on a sick machine
The signal that would have explained the fault simply does not exist
Alerts cannot be joined to work orders, so nothing is ever validated
Cause and effect swap order, and the model learns the relationship backwards
The answer key for every soft sensor is unavailable to the model that needs it
Not one of these is visible on an operator screen. Every one is fatal to a model. Fix the data before buying the algorithm.
Notes: [Slide 22 · 1. AI fundamentals · target 11:04] [11:04–11:07] Three minutes, and it is the most practical slide of the block. Read across the pairs — pathology on the left, consequence on the right. Spend the time on compression. Historians are configured with an exception deviation and a compression deviation, chosen years ago so that screen trends looked clean and disc space lasted. Those settings discard small, slow movements — precisely the signal a degradation model exists to find. Say it plainly: 'Your historian may be deleting the evidence before it is ever stored, and the trend on the screen will look perfectly normal.' The frozen transmitter is the one that frightens people correctly. A stuck input reads a plausible constant, the residual goes to zero, and the model reports perfect health on a degrading machine. Ask the room: 'Does your DCS tag name, your historian point name and your SAP equipment number agree for the same fan?' The laughter is the answer, and it is why alerts cannot be joined to work orders. Land the punch: fix the data before buying the algorithm.

## Slide 23
What changed in your head this hour
Block one close
1. AI fundamentals
23
A threshold asks the wrong question
'Is it above 90 °C' has no context. 'Is it above what it should be at this load and ambient' is the question a model asks.
The residual is the whole idea
Actual minus expected. Anomaly detection, soft sensing and loss attribution are three uses of one arithmetic operation.
Trust is earned on unseen data
A model judged on data it has already seen is a sales figure, not an engineering result. Ask what period it was tested on.
Your data decides the ceiling
Compression settings, frozen transmitters and unhistorised tags cap what any algorithm can do. That work is yours, and it starts before procurement.
Nothing in the next four hours contradicts this hour. It only adds equipment, rupees, and your own hands on the keyboard.
Notes: [Slide 23 · 1. AI fundamentals · target 11:07] [11:07–11:10] Three minutes to close the block. Do not add new material. Take the four cards as a checklist and ask the room to self-assess. 'Card one — could you now explain to a colleague why a fixed threshold asks the wrong question? Card two — could you define a residual in one sentence? Card three — what is the one question you ask a vendor about testing? Card four — name one data pathology at your own station.' If the room can answer those four, the hour has done its job. If a hand goes up on card two, go back to the expected-versus-actual slide for thirty seconds. It is worth the time. The punch line sets up the rest of the day: everything that follows is this same idea with equipment attached, rupees attached, and their own hands on the keyboard. Tell them what is next. After the break, intelligent monitoring — and the first simulation lab, the ID fan bearing case running as real code on a laptop, where they will break the model themselves and watch it happen.

## Slide 24
2
SESSION
From conventional to intelligent monitoring
Why a fixed alarm arrives last, and what a residual sees weeks earlier
The P–F curve and where each technique sits on it
Anomaly detection without the mathematics
The residual pipeline, end to end
Alert quality, and the alert-to-work-order loop
11:25 – 12:10
45 minutes
Hands-on: SIM-1 — residual anomaly detection
24
Notes: [Slide 24 · 2. Intelligent monitoring · target 11:25] [11:25] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 25
The P–F curve, and where each technique sits
From first detectable symptom to functional failure — who notices, and when
2. Intelligent monitoring
25
Material or clearance change begins
Nothing detectable by any instrument
—
Ultrasonic and acoustic emission
The earliest detectable change in the metal
Months
Vibration analysis
Bearing and rotor defect frequencies appear in the spectrum
Weeks to months
Model-based residual monitoring
Several historised signals deviate together from expected
Weeks to months
Oil analysis and thermography
Wear debris in the oil, temperature rise on the surface
Weeks
Audible noise and heat
The operator on rounds notices something has changed
Days
DCS alarm on a fixed threshold
One number finally crosses its setpoint
Hours to days
Functional failure
Trip, or forced outage, on the machine's terms
Zero
Notes: [Slide 25 · 2. Intelligent monitoring · target 11:25] [11:25–11:28] Three minutes. Draw the P–F curve verbally: the fault begins, symptoms become progressively detectable, and functional failure sits at the end. The interval between first detectable symptom and failure is the P–F interval, and every technique in this table sits somewhere inside it. The insight to land: 'Every technique on this ladder is one you already run or already know. AI does not replace any of them. It adds one more rung, using signals you already historise, on equipment where you cannot justify a vibration route every month.' That last clause is the real argument. Vibration analysis is excellent, and it is applied to a small population because it costs skilled time. Residual monitoring runs on every historised machine at once, for almost no marginal effort per machine. Point at the bottom two rows. 'By the time the DCS alarm sounds you have consumed almost the entire interval. That is not a criticism of the alarm. A fixed threshold is a last line, and it is doing exactly what it was designed to do.'

## Slide 26
Why a fixed threshold is structurally late
ID fan drive-end bearing — an illustrative reconstruction, not a MAHAGENCO case study. Same machine and the same numbers as handout 2.2.
2. Intelligent monitoring
26
Chart: Bearing temperature against model-expected
| Wk 0 | Wk 2 | Wk 4 | Wk 6 | Wk 8 | Wk 10 | Wk 12 | Wk 14
Measured (°C) | 74 | 75 | 76 | 78 | 80 | 83 | 86 | 91
Model expected (°C) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
Week 3 — residual +2 °C. Load and ambient are already removed, so this is the machine and not the weather. Nothing on any screen in the control room has changed.
Week 5 — residual +4 °C, sustained across several load points. The system alerts. The bearing reads 78 °C, which is 12 °C BELOW the alarm and has happened normally hundreds of times.
Week 10 — 86 °C on a warm day at full load. An operator finally notices, because now the absolute number looks wrong.
Week 10+ — the DCS alarm at 90 °C. The fan comes out on the fan's terms rather than yours. The alarm was not wrong; a fixed threshold is simply the last thing in the plant to know.
Five weeks of notice against a few days. Why not just lower the alarm to 78? Because 78 is normal at full load in May — you would create a nuisance alarm that is inhibited within a fortnight.
Notes: [Slide 26 · 2. Intelligent monitoring · target 11:28] [11:28–11:32] Walk the chart left to right and let them watch the gap open. These are the same numbers as section 2.2 of the handout, so anyone following along sees one story, not two. The single most important visual point: the expected line stays flat while the measured line climbs. It stays flat because the model has already removed load and ambient. Plot raw bearing temperature instead and it would wander with the weather and you would see nothing at all. The whole story is the widening gap, not the rising line. This is the payoff for the residual idea you set up in slide 8 — deliver the five weeks here, with weight. Ask the room what they would do with five weeks' notice on an ID fan. Somebody will say 'line up the standby and order the shells' — that is exactly the answer, and it is worth more coming from them than from you. Then pre-empt the obvious objection before anyone raises it: why not simply lower the alarm? Because a fixed alarm has one number and the plant has many operating conditions. That is not a configuration failing, it is the structural limit of the method. Be honest about provenance: an illustrative reconstruction, not a MAHAGENCO case study — but the shape is exactly what these failures look like.

## Slide 27
Anomaly detection without the mathematics
What a similarity model actually does, described in plant language
2. Intelligent monitoring
27
1
Build a memory of healthy states
Take a year of known-good operation and keep a library of the operating states the machine actually visited — every load, every season, every fuel.
2
Find the closest matches
For the state the machine is in right now, look up the handful of remembered states that most closely resemble it.
3
Estimate every signal
From those matches, reconstruct what each signal should read now. That is the expected value, and no physics equation was ever written.
4
Watch the gaps
Compare estimate against measurement, signal by signal. Alert only when a gap is both large enough and persistent enough to mean something.
No failure history is required. The model only needs to know what healthy looks like, in every condition the machine actually runs in.
Notes: [Slide 27 · 2. Intelligent monitoring · target 11:32] [11:32–11:35] Three minutes, no mathematics on the slide and none out of your mouth either. The library analogy works well: 'The model keeps a memory of every operating state the machine visited during a healthy year. When you ask what the bearing should read right now, it finds the handful of remembered states most resembling the present one and reconstructs the answer from them. It is closer to an experienced operator saying I have seen this machine in this condition before than it is to any equation.' Stress step four, because credibility lives there. Two tests must be passed before an alert exists: the gap must be large enough, and it must persist. Either one alone produces noise. Land the punch. This is the answer to the objection from the last block — 'we have never had this machine fail, so we have no data to train on.' You do not need failure data. You need one clean year of healthy running. Tell them they are about to do exactly this, themselves, in six minutes.

## Slide 28
One signal moving, or the machine moving
The single most useful discrimination a multi-signal model hands you
2. Intelligent monitoring
28
ONE TAG DEVIATES ALONE
That is instrumentation
Bearing temperature rises, but fan power, lube oil outlet, vibration and discharge pressure all read exactly as expected. Nothing physical can raise one and leave the rest untouched. Check the transmitter and the thermocouple before you touch the machine.
A COHERENT GROUP DEVIATES
That is the machine
Bearing temperature, lube oil outlet, vibration and motor current all move together in the direction physics predicts. Not one has crossed an alarm limit. The pattern is the evidence, and it appears weeks before any individual number does.
Which of the two it is decides who you send: the instrument technician, or the mechanical engineer with a spare bearing. No single-tag alarm can tell you that.
Notes: [Slide 28 · 2. Intelligent monitoring · target 11:35] [11:35–11:38] Three minutes, and this is the discrimination engineers value most once they have it. Say it as a physical argument rather than a statistical one: 'Nothing physical can raise a bearing temperature and leave the fan power, the lube oil outlet, the vibration and the discharge pressure all exactly where they should be. If one signal has moved and its physical neighbours have not, you have an instrumentation problem, and you should check the transmitter before you touch the machine.' Then the reverse: 'When four signals move together in the direction physics predicts, and not one of them has crossed an alarm limit, that is the machine telling you something weeks before any single number will.' Ask the room how much time their station spends chasing single-tag alarms that turn out to be thermocouples. Every station has this problem, and this is the first thing multi-signal monitoring gives back — hours that were being spent on instrumentation, not machines. Land the punch and move on. They will see this in the lab shortly.

## Slide 29
The residual pipeline, end to end
Everything between a tag in the historian and an engineer picking up the telephone
2. Intelligent monitoring
29
SIGNAL CONDITIONING
Tag values
bearing, load, ambient, oil, power
Validate
range, freeze, rate-of-change checks
Operating mode
start-up, low load, normal, shutdown
Similarity model
find the closest healthy states
DETECTION
Expected value
per signal, right now
Residual
actual minus expected
Smooth and persist
EWMA, then N days above threshold
Rank and group
one alert per machine, not per tag
THE HUMAN LOOP
Alert with evidence
which signals, how far, since when
Engineer triages
fault, sensor, or operating condition
Action raised
inspection or work order
Finding recorded
what was actually found
Feedback: Findings return to tune thresholds, remove false-alarm sources and curate the next training window
12 steps. Exactly one of them is the machine learning. The other 11 decide whether it works.
Notes: [Slide 29 · 2. Intelligent monitoring · target 11:37] [11:37–11:41] This is the slide to photograph. It is the whole of Session 2 on one page. Move through it steadily. At 'Validate', remind them a frozen transmitter reads a perfectly plausible constant and the model will believe it. At 'Operating mode', link back to the segmentation slide. At 'Rank and group', make the point that alerting on every tag is how you generate eleven alerts a week and lose the shift. The punch line is the argument of the whole day: one box out of 12 is the algorithm. Vendors sell that one box. The other ten are yours. End on the feedback arrow and hand over to the lab — SIM-1 is exactly the middle lane of this diagram, made interactive.

## Slide 30
Operating modes — why one model is never enough
A model trained only on full load will scream through every single start-up
2. Intelligent monitoring
30
The problem
Start-up, low load, full load and shutdown are physically different machines. A residual computed against full-load behaviour is meaningless during a ramp.
Segmentation
Detect the mode first — from load, mill combination and firing state — then apply the model built for that mode. Suppress alerts during transitions you have not modelled.
Why it is first-order here
Units designed for baseload now two-shift and run at technical minimum. Transitions are no longer rare events; they are a large part of the month.
The design consequence
Budget for several models per machine and a written rule for which one is live. That is engineering work, not a configuration screen.
If a vendor demonstration only ever shows steady full load, ask to see a start-up. The answer tells you how much work is left.
Notes: [Slide 30 · 2. Intelligent monitoring · target 11:38] [11:38–11:41] Three minutes. This is the design point that separates a demonstration from a working system. Say it directly: 'A model trained only on full-load steady operation will scream through every start-up, every ramp and every night at technical minimum. Not because anything is wrong, but because it has never seen the machine in that condition, so everything looks abnormal to it.' Make the cycling point personal to this fleet. Units designed for baseload now two-shift and run at technical minimum. Transitions are no longer rare. A design that treats them as exceptions to be suppressed will end up suppressed for most of the month, and then it is monitoring nothing. The practical consequence is card four: budget for several models per machine, and a written rule for which one is live at any moment, with a name against it. Give them the test on the punch line. 'If a vendor demonstration only ever shows steady full load, ask to see a start-up.' They will not be expecting the question, and how they answer tells you everything.

## Slide 31
Lab — SIM-1 · Residual anomaly detection
Twelve minutes at the keyboard, on the ID fan bearing case we have just walked through
2. Intelligent monitoring
31
SIM-1
Residual anomaly detection — ID fan bearing
12 minutes at your laptop
Do this
Open SIM-1 and run the default case. Write down the lead time the residual gives you against the 90 °C fixed alarm.
Drag the residual threshold down, step by step. Watch the lead time improve and the false alarm count climb with it.
Set persistence to 1 day and re-run. Count how many single-sample spikes now raise an alert.
Put persistence back to 3 days and settle on a threshold you would be willing to defend in a morning meeting.
Tick 'train on contaminated history' and run again. Watch what happens to the detection.
Watch for
The residual crosses its threshold weeks before the measured temperature reaches 90 °C.
Every reduction in threshold buys lead time and costs false alarms. There is no setting that gives you both.
At one day of persistence, sensor spikes become alerts; at three days, they do not.
Trained on contaminated history, the model treats the fault as normal and raises nothing at all.
Two lessons, proven rather than asserted: a residual sees the fault weeks before a fixed threshold, and a model trained on history that already contained the fault will never detect it. Both were claims this morning. Now they are yours.
Notes: [Slide 31 · 2. Intelligent monitoring · target 11:41] [11:41–11:53] [LAB] Twelve minutes at the keyboard. Get them into SIM-1 quickly — the file is on the desktop, opens in any browser, no login and no internet needed. Set it up in one sentence: 'This is the ID fan bearing you just saw on the chart, except now the similarity model is genuinely running in your browser on realistic data. Nothing here is an animation.' Read the five moves aloud before they start, then let them work. Walk the room. Sit with anyone who has not got the default case running within two minutes. The moment that matters is the last one. When they tick 'train on contaminated history' the detection collapses — the model has learned the fault as normal and reports a healthy machine all the way to failure. Stop the room there and make somebody describe out loud what they have just seen. That is this morning's lesson, proven on their own screen. Reconvene at eleven fifty-three sharp. Ask two people what threshold they settled on and why. There is no correct answer, and that is exactly the point.

## Slide 32
Alert quality — the numbers that decide adoption
Measure the programme the way the shift engineer actually experiences it
2. Intelligent monitoring
32
Measure | What it means | Healthy | Failing | Who judges it
Lead time | Warning before the conventional alarm or the failure | Weeks | Hours | Maintenance planning
False alarms per model-month | Alerts raised with nothing to find | Below one | Several a week | The engineer who chases them
Precision on actioned alerts | Share of investigated alerts that found something | Most of them | A small minority | Station leadership
Actionability | Does the alert name a signal, a reason and a next step | Always | A number only | The shift engineer
Time to triage | How long an alert sits before somebody looks at it | Same day | Weeks | The named owner
Feedback closure | Findings written back against the alert | Every one | Almost none | The programme owner
₹100.87 crore
cumulative fixed-charge disallowance for availability shortfall across the fleet — what late detection actually costs us
Notes: [Slide 32 · 2. Intelligent monitoring · target 11:53] [11:53–11:56] Three minutes. This is the specification for the programme, written in the language of the person who has to live with it. Read the failing column down on its own — hours of warning, several false alarms a week, a small minority of alerts finding anything, a number with no reason attached, alerts sitting for weeks, findings never written back. That is a real description of a monitoring programme in its second year, and it is how they die. Define false alarms per model-month again, because it is the one number to put in a contract: one model, one machine, one month. Below one is livable. Several a week, multiplied across a fleet of models, is unmanageable. The stat card is verified from the June 2026 position: ₹100.87 crore of cumulative fixed-charge disallowance for availability shortfall, of which ₹32.93 crore was adjusted in the June 2026 bill alone. That is what late detection costs, and it is the company's own money, not an assumption. Say the hard line: an alert nobody acts on is worse than no alert, because it spends the credibility the next one will need.

## Slide 33
What intelligent monitoring can and cannot detect
Be as precise about the right column as the left, or the first miss ends the programme
2. Intelligent monitoring
33
It will catch this
It will not catch this
Slow degradation with a signature in historised tags
A failure with no measured signal anywhere near it
Fouling, wear, leakage, blockage, loss of cooling
A sudden mechanical break with no precursor at all
A group of signals drifting quietly together
A fault the model was trained through and learned as normal
A transmitter that has stopped responding
A transmitter wrong in a physically plausible way since day one
Behaviour unlike anything in the healthy history
Any operating condition the training year never contained
A machine degrading over weeks
A machine failing in the next ten seconds — that is the protection system's job
It buys weeks on degradation. It buys nothing on sudden failure, and claiming otherwise is how programmes lose their credibility.
Notes: [Slide 33 · 2. Intelligent monitoring · target 11:56] [11:56–11:59] Three minutes, and it is a credibility slide. Be as precise about the right column as about the left. The reason to be this explicit: the first miss defines the programme. If nobody has said out loud what the system cannot see, then the first sudden failure will be presented in a review meeting as proof that the whole thing does not work. Take row four carefully, because it is the subtle one. A transmitter that stops responding is easy to catch, because its neighbours keep moving and the model notices. A transmitter that has been quietly wrong in a physically plausible way since commissioning is nearly invisible, because the model simply learned the wrong value as normal. Read the last row twice: 'A machine degrading over weeks, against a machine failing in the next ten seconds — that is the protection system's job.' This ties straight back to this morning. Two layers, different work, neither substituting for the other. Ask the room for a failure at their own station that this would not have caught. Take the answer seriously. It builds more trust than any success story.

## Slide 34
The five ways monitoring quietly stops working
Every one of these leaves the dashboard looking perfectly healthy
2. Intelligent monitoring
34
Compression
Historian compression and exception deviation tuned for clean screen trends discard exactly the slow drift the model exists to find. The trend still looks fine; the evidence has been thrown away.
Frozen transmitter
A stuck input reads a plausible constant. The residual falls to zero, the model reports perfect health, and the machine degrades unwatched behind it.
Timestamp misalignment
Unsynchronised clocks across DCS, historian and lab shift signals against one another. The model learns cause and effect in the wrong order and its estimates decay.
Post-overhaul drift
After an overhaul the machine is genuinely different. An un-retrained model alarms continuously, is disbelieved, and is switched off inside a month.
Silent tag loss
A point stops updating after a system change and nobody notices, because no alarm exists anywhere for a tag that has simply gone quiet.
Never assume a quiet model means a healthy machine. Check for: frozen inputs · dead tags · unchanging residuals · models not retrained since the last overhaul
Notes: [Slide 34 · 2. Intelligent monitoring · target 11:59] [11:59–12:02] Three minutes. Every one of these leaves the dashboard looking healthy, which is exactly what makes them dangerous. Compression first, because it is the most common and the least suspected. Exception deviation and compression deviation were set years ago for clean screen trends and manageable disc space. Those settings discard small, slow movements — precisely the signal a degradation model exists to find. Say it plainly: 'The evidence may be deleted before it is ever stored, and the trend on your screen will look perfectly normal.' The frozen transmitter is the one to dwell on: residual to zero, model reports perfect health, machine degrades unwatched. A monitoring system must therefore monitor its own inputs — a signal that has not changed in six hours is itself an alert. Post-overhaul drift is the organisational one. After an overhaul the machine is genuinely different. An un-retrained model alarms continuously, is disbelieved, and is switched off inside a month — and nobody ever records that it was switched off. Land the closing line: a quiet model is not evidence of a healthy machine until you have checked why it is quiet.

## Slide 35
The alert-to-work-order loop
The technology is the easy part. This loop decides whether the programme is alive in a year.
2. Intelligent monitoring
35
1
Model raises an alert
With the evidence attached: which signals moved, how far from expected, since when, and what share of the deviation each one explains.
2
An engineer triages it
Real fault, sensor problem, or an operating condition the model has never seen? A named engineer, daily, with time allocated. Not a committee.
3
Action is raised
An inspection, a condition check, or a work order in SAP — with the alert reference carried into the notification so the two can be joined later.
4
The finding is written back
What was actually found, and when — including 'nothing found'. This is the step every programme skips and the only one that makes the model better.
5
The model improves
Thresholds are tuned to this particular machine, known false-alarm sources are removed, and real fault signatures are learned so they are recognised faster the next time round.
↺ findings return to the model
A monitoring programme without step four dies within a year. Every time, at every station, without exception.
Notes: [Slide 35 · 2. Intelligent monitoring · target 12:02] [12:02–12:05] Slow down here. This slide is the difference between a working programme and an expensive dashboard. Step two: 'A named engineer, daily, with time allocated in their day. Not a committee, not a vendor, not whoever happens to be free.' If nobody owns triage, alerts accumulate and within two months everybody stops opening them. Step four is the one that always fails. Ask the room directly: 'When a condition-monitoring alert leads to an inspection at your station, does the finding ever get written back against that alert?' The honest answer is almost always no. Then explain the consequence — the model never learns which alerts were worth raising, so the false-alarm rate never falls, so trust never builds, so the programme dies. Say explicitly that 'nothing found' is a valuable finding and must be recorded. Most programmes only capture the hits, which biases everything that follows. The punch is a prediction, not a warning. Ask them to hold that sentence in mind when the first vendor proposal arrives with no mention of step four.

## Slide 36
Fleet-scale monitoring
One model per machine becomes hundreds of models across five stations
2. Intelligent monitoring
36
The arithmetic
One model per fan, mill, pump, motor and heat exchanger. A single unit reaches dozens. Five stations reach several hundred. Indicative — but the order is right.
Nobody watches hundreds of screens
At fleet scale the output must be one ranked daily list, worst deviation first with the evidence attached — not a dashboard per machine.
Ownership must be named
Each model needs an owner at the station, and the fleet needs one owner of the method. Unowned models get switched off quietly, within months.
A model is a configured asset
It needs a register, a version, its training period on record, a retraining trigger and a review date — the same discipline as a protection setting.
Stations are not interchangeable
Khaperkheda Units 1-4 ran at 57.85 % availability in June 2026, Parli Unit 8 at 97.40 %. The same model does not transfer between them.
Governance beats algorithms
Fleet programmes fail on registers, ownership and retraining — not on mathematics. Budget for the administration, or do not start.
Hundreds of models is a governance problem wearing an engineering costume. Decide who owns them before you buy them.
Notes: [Slide 36 · 2. Intelligent monitoring · target 12:05] [12:05–12:08] Three minutes. This is the slide for the people in the room who will have to run this across stations, not just on one machine. Be honest that the model count is indicative — the order of magnitude is what matters. One model per fan, mill, pump, motor and heat exchanger reaches dozens on a single unit and several hundred across five stations. The card that changes behaviour is the third. Say: 'Every one of these models needs an owner at the station, and the method needs one owner across the fleet. A model with no owner gets switched off quietly, and nobody writes it down.' Use the verified contrast on card five. Khaperkheda Units 1 to 4 ran at 57.85 per cent availability in June 2026; Parli Unit 8 at 97.40 per cent. Same company, same month, entirely different duty and condition. A model does not transfer between them without retraining, and anyone who says otherwise has not tried it. Land the punch: hundreds of models is a governance problem wearing an engineering costume.

## Slide 37
Three things to take to lunch
Block two close
2. Intelligent monitoring
37
A residual sees weeks; a threshold sees days
You proved it at the keyboard in SIM-1. The gap between the two is the entire business case for intelligent monitoring.
A model is only as honest as its training period
Contaminate the healthy history and detection collapses completely. You did not take that on trust — you watched it happen.
Without the feedback step, the programme dies
Alerts that are never closed out teach the model nothing, and teach the engineer to stop opening them.
After lunch
We put rupees on it — heat-rate loss attribution and auxiliary power, worked on MAHAGENCO's own June 2026 numbers.
₹100.87 crore of fixed-charge disallowance and ₹56 crore of heat-rate gap in a single month are waiting on the other side of lunch.
Notes: [Slide 37 · 2. Intelligent monitoring · target 12:08] [12:08–12:10] Two minutes, then lunch. Do not introduce anything new and do not run over — the room is already thinking about food. Take the three takeaways as statements they proved themselves rather than things you told them. 'You did not take my word for the lead time — you measured it in SIM-1. You did not take my word that the training period matters — you broke the model yourself and watched the detection disappear.' The third card is the one to leave hanging. Without the feedback step the programme dies. Say it once, and let it sit. Then set up the afternoon in a single sentence: after lunch we stop talking about equipment and start talking about money — heat-rate loss attribution and auxiliary power, on MAHAGENCO's own June 2026 numbers, with ₹56 crore of net heat-rate gap in one month and ₹100.87 crore of fixed-charge disallowance on the table. Give them the exact time to be back, and then finish early.

## Slide 38
3
SESSION
AI for predictive maintenance
Boiler feed pumps, mills, fans, transformers and motors — and the availability money behind them
Equipment by equipment: what is detectable and how early
Remaining useful life, and the question a planner actually asks
What predictive maintenance needs from the organisation
₹100.87 crore of availability disallowance, and where it came from
12:10 – 13:00
50 minutes
Hands-on: SIM-5 — predictive maintenance and RUL
38
Notes: [Slide 38 · 3. Predictive maintenance · target 12:10] [12:10] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 39
Maintenance strategies compared
Four positions on one ladder — and most stations are two rungs lower than they believe
3. Predictive maintenance
39
Strategy | What triggers the work | What it costs you | Where it fits
Breakdown — run to failure | The machine stops | Collateral damage, long outage, no spare staged | Cheap, duplicated, non-critical items only
Time-based — calendar or running hours | The date arrives | Good machines opened; bad ones fail before the date | Statutory items and known wear-out parts
Condition-based — measure, then decide | A measured parameter crosses a limit | Route data monthly; the fault can start the day after | Vibration routes, oil analysis, thermography
Predictive, then prescriptive | A model projects a limit will be crossed | Data plumbing, a triage engineer, and discipline | Rotating plant with continuous data
Prescriptive is the next rung: not only when it will fail, but which action costs least. Nobody reaches it from row one.
Notes: [Slide 39 · 3. Predictive maintenance · target 12:10] [12:10–12:14] Open the block by asking the room to place their own station on this ladder, honestly. Most will say condition-based. Then ask the follow-up: how often is the vibration route actually walked, and what happens to the readings afterwards. That usually moves the answer back a rung. Work down the third column. Row one costs you collateral damage and a spare nobody staged. Row two costs you healthy machines opened on a calendar. Row three is genuinely good engineering, but the sampling interval is monthly and the fault does not consult the schedule. Row four is what changes: the same measurement, taken continuously, with a model that projects forward instead of comparing to a limit. Be clear about what row four costs. Not a large capital sum — data plumbing, one engineer who owns triage, and the discipline to close every alert. That is the honest price, and this block will keep returning to it. Land the punch. Prescriptive maintenance answers which action costs least, not merely when. It is real, and no station reaches it directly from row one.

## Slide 40
Case — boiler feed pumps
Motor-driven on the 210 and 250 MW units, turbine-driven on the 500 and 660 MW machines
3. Predictive maintenance
40
What the model detects
Bearing degradation — thrust and journal, weeks ahead of temperature alarm
Mechanical seal wear, seen in leak-off flow and temperature
Cavitation and loss of NPSH margin at low suction pressure
Recirculation valve passing, sticking or opening late
Hydraulic performance drift — head developed falling at the same speed and flow
Coupling wear and shaft alignment deterioration
Balance drum and balancing disc wear, seen in axial position and leak-off
Signals it uses
Suction and discharge pressure, differential head, feed flow
Motor current and power, or turbine steam flow and speed on a TDBFP
Bearing metal and oil temperatures, shaft vibration and axial position
Seal leak-off flow, temperature and seal water differential pressure
Recirculation valve position and demand, and its response time
Deaerator level, suction temperature and calculated NPSH available
Typical lead time
Bearing and seal problems typically show in the residual weeks before a temperature alarm; hydraulic drift shows in months and is almost never noticed at all.
Proven — the most reliable predictive application on the feedwater side
Watch out: Do not use one model for both drive types. A turbine-driven pump on a 660 MW unit has speed as a free variable; a motor-driven pump does not. Their normal behaviour is genuinely different and one model will fit neither.
Notes: [Slide 40 · 3. Predictive maintenance · target 12:14] [12:14–12:17] Start with the room's own experience. Ask how many BFP-related trips or load restrictions their station has had in the last two years. On a fleet this size the hands will go up quickly. Walk the detects list, but spend the time on the last two. Hydraulic performance drift and balance drum wear are the ones nobody watches, because there is no alarm for them and no route reading that captures them. Developed head at a given speed and flow falls slowly over months. A model sees that; a shift engineer cannot. Make the signals point concrete: everything in that list is already in the historian. This case needs no new instrument on most units. The caution is the engineering point of the slide, and it applies to every case that follows. A turbine-driven pump has speed as a free variable, so its power and flow relationship is fundamentally different from a motor-driven pump running at fixed speed. One model across both drive types learns the average of two machines and represents neither.

## Slide 41
Case — coal mills and pulverisers
The plant item that most often decides whether a unit holds load
3. Predictive maintenance
41
What the model detects
Grinding element and roller wear, trended as current per tonne of coal
Mill choking, hours before it happens, from differential pressure behaviour
Fineness deterioration between sampling campaigns
Feeder calibration drift — the mill says one tonnage, the boiler says another
Classifier setting problems and seal air differential loss
Mill fire precursors — outlet temperature rise with falling coal flow
Signals it uses
Mill motor current and power, and the ratio to feeder tonnage
Mill differential pressure and primary air flow and temperature
Mill outlet temperature and the cold-air damper demand
Grinding or hydraulic loading pressure and roller position
Seal air to mill differential pressure
Reject rate, mill vibration and bowl or table speed
Typical lead time
Choking is predictable hours ahead from differential pressure and current behaviour. Grinding element wear trends over months and tells you what to stage for the next outage.
Proven — high value, because a mill trip is a load restriction
Watch out: Build one model per mill, never one per unit. Mills on the same boiler have different wear, different coal splits and different air balance. A unit-level model averages six machines and hides the one that is degrading.
Notes: [Slide 41 · 3. Predictive maintenance · target 12:17] [12:17–12:20] Mills are where this audience will engage hardest, so let them talk. Ask what fraction of their load restrictions in the last year traced back to a mill. The single most useful idea on this slide is a ratio, not an algorithm: mill current per tonne of coal. Current alone tells you nothing because it moves with feed rate. Current per tonne holds across the load range and climbs steadily as grinding elements wear. Anybody in this room can plot that tomorrow in the historian with no AI at all — and almost nobody does. On choking, be precise. Differential pressure and current start behaving abnormally hours before the mill actually chokes. That is not a threshold crossing, it is a change in pattern, which is exactly what a residual model detects. Read the caution aloud and dwell on it. One model per mill, not per unit. Six mills on one boiler have different coal splits, different air balance and different wear. Averaging them is precisely how you hide the one that is failing.

## Slide 42
Case — ID, FD and PA fans
Large rotating plant, continuously instrumented, and directly on the auxiliary power bill
3. Predictive maintenance
42
What the model detects
Blade and impeller erosion from ash, seen as efficiency drift
Unbalance developing from uneven erosion or ash build-up
Bearing wear on both fan and motor, ahead of temperature alarm
Damper, inlet guide vane and blade-pitch actuator problems
Approach to surge or stall on axial fans, before it is audible
Duct and expansion joint leakage, seen as flow that does not arrive
Fan efficiency drift — power rising for the same gas flow
Signals it uses
Motor current and power, and fan speed where variable
Inlet and outlet pressure, differential head across the fan
Gas or air flow, and furnace draught
Bearing vibration, shaft displacement and bearing temperatures
Damper, IGV or blade-pitch position demand and feedback
APH inlet and outlet gas temperature and oxygen, for leakage context
Typical lead time
Bearing and unbalance faults appear in the residual weeks ahead. Efficiency drift from erosion is a months-long trend and is the one that costs money continuously.
Proven — and the easiest place to connect maintenance to auxiliary power
Watch out: Fan power against gas flow is the cheapest health indicator in the plant, needs no new instrument and no model, and almost nobody plots it. Ask your performance engineer for that curve for last year before you buy anything.
Notes: [Slide 42 · 3. Predictive maintenance · target 12:20] [12:20–12:23] Fans matter twice over. They fail and take the unit down, and they consume a very large share of the auxiliary power bill we will read after lunch. Say that link explicitly — it sets up Block 4. On axial fans, be careful and precise. Approach to surge is a pattern in pressure and flow that a model can flag before it becomes audible, but nothing in this course sits in the surge protection loop. Detection and protection are different systems. The caution is the line to make them write down. Fan power against gas flow, plotted for a year, is free. Every signal is already in the historian, there is no algorithm, and it shows erosion and internal fouling as a slow upward drift in power for the same duty. Ask the room, directly: has anybody here seen that curve for their own ID fans? Usually nobody has. That is the honest state of the art in most stations, and it is a better first step than any procurement.

## Slide 43
Case — transformers and switchyard
Identical equipment at all five stations, and the highest consequence per failure
3. Predictive maintenance
43
What the model detects
Dissolved gas trends and ratios, not single values against a limit
Winding hot spot running above what the thermal model predicts
OLTC contact wear, from motor current signature during a tap change
Bushing capacitance and tan delta drift, well before failure
Cooling bank underperformance — fans or pumps running with no effect
Moisture ingress and accelerated paper ageing at sustained high load
Signals it uses
Dissolved gas concentrations and their rate of change over months
Top oil and winding temperatures, load current and ambient
Cooler bank status, fan and pump currents, oil flow indication
OLTC motor current profile, operation counter and drive time
Bushing leakage current or online tan delta where fitted
Partial discharge, where online monitoring is installed
Typical lead time
Gas trends and bushing drift develop over months. The lead time is long, which is exactly why the sampling interval, not the algorithm, is usually the limiting factor.
Proven — dissolved gas trending is the oldest predictive technique in the industry
Watch out: Six-monthly manual sampling cannot produce a trend. Two points a year tell you almost nothing about a rate of change, and rate of change is the whole diagnosis. Fix the sampling interval before anybody discusses an algorithm.
Notes: [Slide 43 · 3. Predictive maintenance · target 12:23] [12:23–12:26] This is the case with the highest consequence per event and the longest warning time, so it is worth the three minutes even though it is the least fashionable. Make the first bullet the headline. Dissolved gas analysis judged against a single limit is a pass or fail test. Judged as a trend with ratios, it is a diagnosis — it distinguishes overheating from arcing from partial discharge. Same data, entirely different value. The OLTC point usually surprises people, so explain it. The tap changer motor draws a characteristic current profile through each operation. Contact wear, mechanism binding and spring problems change the shape of that profile long before anything fails. It is the same idea as motor current signature analysis, applied to a mechanism. Read the caution and stop there. If your station samples oil twice a year, you have two data points and no trend. No model recovers information that was never sampled. Increasing sampling frequency, or fitting online DGA on the critical units, is the project — not the analytics.

## Slide 44
Case — HT and LT motors
Hundreds per unit, and the electrical signal itself is the sensor
3. Predictive maintenance
44
What the model detects
Broken or cracked rotor bars and end-ring faults, from current sidebands
Static and dynamic eccentricity in the air gap
Bearing defect frequencies, visible in current as well as vibration
Stator insulation deterioration, from partial discharge and unbalance trends
Supply quality — voltage unbalance, harmonics and their heating effect
Driven-equipment problems seen through the motor, without instrumenting the machine
Cooling degradation — blocked coolers and rising winding temperature at constant load
Signals it uses
Stator current waveform at high sample rate, not an averaged value
Supply voltage, unbalance and harmonic content
Winding and bearing temperatures, and cooling air or water temperature
Vibration where fitted, for cross-confirmation of a current-based finding
Load context — driven equipment flow, pressure or tonnage
Start counts, run hours and starting current profile
Typical lead time
Rotor bar and eccentricity faults are detectable months ahead. The technique is mature; the obstacle is almost always the data path, not the mathematics.
Proven — motor current signature analysis is decades old and well validated
Watch out: Historian averages destroy this. The sidebands MCSA depends on sit close to the supply frequency and vanish the moment current is stored as a one-minute average. This case needs edge processing near the machine, not a historian tag.
Notes: [Slide 44 · 3. Predictive maintenance · target 12:26] [12:26–12:29] This case teaches a data lesson that applies far beyond motors, so make sure the caution lands. Explain the principle in one sentence: a fault in the rotor modulates the stator current, producing small sidebands very close to the supply frequency, and their size tells you how many bars are broken. The motor is its own sensor. No accelerometer, no shutdown, no access. Then make the obstacle explicit. Those sidebands live at a few hertz either side of fifty. To see them you need current sampled at kilohertz rates. Your historian stores a one-minute average, and a one-minute average has thrown away every trace of them before the data ever reaches a model. Ask the room what resolution their historian actually stores for motor current. Most will not know, and that is a genuinely useful thing to go and find out on Monday. Land the general lesson. The data you have is not always the data the technique needs. Some applications require processing near the machine. Recognising which ones is an engineering judgement, and it is yours to make.

## Slide 45
Case — ESP, ash handling and CHP conveyors
A large share of the maintenance effort, and almost none of the instrumentation
3. Predictive maintenance
45
What the model detects
ESP field energisation drift and rapping that has stopped being effective
Hopper ash build-up and choking, predicted from evacuation cycle times
Ash slurry and vacuum pump wear, from current and cycle duration
Conveying line blockages, from vessel fill and empty times lengthening
Conveyor belt misalignment, idler seizure and drive slip
Transfer chute and crusher choking in the coal handling plant
Wagon tippler and stacker-reclaimer mechanism degradation
Signals it uses
ESP field kV, mA and spark rate, per field, and stack opacity
Ash vessel fill and evacuation cycle times, and valve operation counts
Conveyor motor current, belt drift switch operations and pull-cord events
Bearing temperatures and vibration on drive and tail pulleys
Crusher and ring granulator current, and screening throughput
Cycle counts and run hours, which most stations already log somewhere
Typical lead time
Cycle-time drift is the earliest and cheapest indicator here, and it is usually already recorded in the PLC without anybody trending it.
Emerging in practice — the technique is simple, the instrumentation is the gap
Watch out: This plant consumes a large share of the station's maintenance effort and is rarely instrumented for analytics at all. The first project here is not a model. It is getting cycle times and motor currents into the historian.
Notes: [Slide 45 · 3. Predictive maintenance · target 12:29] [12:29–12:32] This is deliberately the unglamorous slide, and it is the one most likely to be true of everybody's station. Ask the room a blunt question: what proportion of your maintenance man-hours goes to ash handling, coal handling and the ESP? The answer is usually far higher than anybody expects, and far higher than the analytics attention these systems receive. The teaching point is that the technique here is trivial. Cycle-time drift — a vessel that used to evacuate in ninety seconds now taking a hundred and forty — is a first-year statistics problem, not machine learning. The obstacle is that the number is sitting in a PLC and never reaches a historian. On the ESP, connect it forward to Block 4. Field energisation is both a maintenance question and an auxiliary power question, and after lunch we will see the auxiliary bill for the whole fleet. Land the caution honestly. For this equipment, the first project is instrumentation and data collection, not analytics. Say that plainly — it protects the audience from being sold a model that has nothing to run on.

## Slide 46
Diagnostics versus prognostics
Two different questions, two different levels of confidence, two different audiences
3. Predictive maintenance
46
DIAGNOSTICS
What has changed?
The residual on the thrust bearing is six degrees and growing, and the model points at that signal rather than at load or ambient. It names the machine, the signal and often the direction. It is a question about the present, and an engineer can go and check it.
PROGNOSTICS
How long have I got?
The same residual, fitted with a degradation curve and projected forward to a functional failure threshold. It answers a planning question rather than a diagnostic one, and it arrives with an uncertainty band that is usually wide. Wide is not useless. Wide is honest.
Diagnostics tells you to look. Prognostics tells you whether to book the outage. Most stations need the first far more than they currently think they need the second.
Notes: [Slide 46 · 3. Predictive maintenance · target 12:32] [12:32–12:35] Three minutes, and the whole slide exists to stop a common procurement mistake. Say the two questions aloud as questions. What has changed? How long have I got? They sound similar and they are not. The first is answered from data you already have, with confidence an engineer can verify by walking to the machine. The second requires a model of how the damage progresses, and that model carries far more uncertainty. Ask the room which question their morning meeting actually asks. In practice it is almost always the first — what is wrong with this machine — and that is the honest place to start. Make the commercial warning explicit. Vendors sell prognostics because a date sounds more valuable than an alert. In a station with no reliable residual monitoring, buying prognostics is buying the roof before the walls. Land the punch. Get diagnostics working, trusted and closing into work orders first. Prognostics is the second year of the programme, not the first.

## Slide 47
Remaining useful life, and why a point estimate is the wrong answer
The number a planner can actually act on is a probability, not a date
3. Predictive maintenance
47
Sixty-two days is not an answer
A single number invites either complacency or panic. No planner commits an outage window to it, and no engineer defends it in a review.
The band carries the information
A projection with a ninety per cent range tells you what you can commit to. The width of that band is the message, not an apology for it.
Ask the planner's question instead
What is the probability this machine survives to the outage already in the plan? That question has a usable answer and a rupee value attached.
What makes the band open
A short trend history, a noisy measurement, and a failure threshold nobody has ever measured. The first of those is the cheapest to fix.
More history beats a better algorithm
Thirty days of trend cannot separate fast degradation from slow degradation with noise on it. No algorithm recovers what was never observed.
Statistical error is not model error
The band covers uncertainty in fitting the curve. It says nothing about the curve being the wrong shape, which is usually the larger risk.
Remaining useful life is a distribution, not a date. Anyone quoting a single number has already hidden the part you needed.
Notes: [Slide 47 · 3. Predictive maintenance · target 12:35] [12:35–12:38] This slide sets up the lab, so keep it moving and let the software prove the point. Start with the first card as a piece of theatre. Say: 'The bearing has sixty-two days left.' Then ask the room what they would actually do with that sentence. Somebody will say plan the outage at day fifty. Ask them how confident they are in the sixty-two. Nobody knows, because nobody was told. Now reframe it with the third card. The planner does not need a date. The planner needs to know whether this machine reaches the outage that is already in the plan, and what it costs if it does not. That is a probability and an expected cost, and both are computable. The fifth card is the one they will prove for themselves in three minutes. Thirty days of trend genuinely cannot distinguish a fast degradation from a slow one with noise on it. Be honest about the last card. The uncertainty band is statistical only. If the degradation mechanism is not the one assumed, the band is confidently wrong.

## Slide 48
Lab — SIM-5 · Predictive maintenance and remaining useful life
Ten minutes at the keyboard, on the station carrying the largest disallowance in the fleet
3. Predictive maintenance
48
SIM-5
Predictive maintenance and remaining useful life
10 minutes at your laptop
Do this
Open SIM-5 and select Koradi Units 8-10 — the station carrying ₹28.04 crore of disallowed fixed charge.
Read two figures only: the probability of surviving to the planned outage, and the expected cost of waiting against the cost of acting now.
Drag 'days of trend observed' down to 30 and watch the projection band open up. Do not change anything else.
Put it back to 70, then move the planned outage date further out and closer in, and watch the recommendation flip.
Set the forced-outage duration to a figure your own station would recognise, and see what that does to the asymmetry.
Press 'New machine' twice. The same settings give a different answer, because the trend is a different sample.
Watch for
The remaining-life figure moves very little when you shorten the trend, but the ninety per cent range widens dramatically.
The decision table is driven by the survival probability, not by the point estimate of remaining life.
Moving the planned outage flips the recommendation with no change to the machine or its degradation at all.
The cost of a forced outage carries a share of the fixed-charge disallowance the station is already paying.
The point estimate barely moves; the uncertainty band moves enormously. That is the lesson. A planner acts on the probability of reaching the outage already scheduled, and that number is worth more than any single date.
Notes: [Slide 48 · 3. Predictive maintenance · target 12:38] [12:38–12:48] [LAB] Ten minutes, and it is the last activity before lunch, so start it briskly and keep the clock visible. Frame it in one sentence: 'This is an exponential degradation model with a recursive parameter update, running in your browser on this station's own variable charge and its own disallowance figure. The rupees are real MAHAGENCO numbers.' Read the six moves aloud before anybody touches the keyboard. Move three is the one that matters. When they drag days of trend observed down to thirty, the estimate of remaining life hardly changes but the ninety per cent band opens right up. Stop the room there and ask somebody to describe what they are looking at. The answer you want is that a short window cannot tell a fast degradation from a slow one with noise on it. Move four is the second lesson. The same machine and the same trend produce opposite recommendations depending on when the next outage is. Remaining useful life only becomes a decision when it meets the outage plan. Reconvene at twelve forty-eight. Take one answer from the room, then break for lunch.

## Slide 49
The availability arithmetic
What unavailability already cost us — June 2026, from our own bill
3. Predictive maintenance
49
Station | Availability % | Normative % | AFC disallowance ₹ cr | Reading
Koradi Units 8-10 | 72.50 | 85.00 | 28.04 | Largest single loss in the fleet
Chandrapur Units 3-7 | 64.88 | 80.00 | 23.94 | Lower norm, still far short
Khaperkheda Units 1-4 | 57.85 | 85.00 | 21.75 | Lowest availability in the fleet
Chandrapur Units 8-9 | 74.87 | 85.00 | 11.75 | Newer units, same shortfall
Bhusawal Unit 6 | 79.01 | 85.00 | 7.88 | Six points from the norm
Paras Units 3-4 | 74.83 | 85.00 | 5.74 | Ten points from the norm
Koradi Unit 6 | 75.46 | 75.00 | 0.25 | Norm is 75 % — essentially met
Parli Unit 8 | 97.40 | 85.00 | 0.00 | Fleet best — the norm is achievable
₹100.87 crore
cumulative fixed-charge disallowance for availability shortfall, of which ₹32.93 crore was adjusted in June alone
Notes: [Slide 49 · 3. Predictive maintenance · target 12:48] [12:48–12:52] Come back from the lab straight into the company's own money. This is the slide that connects everything in this block to the regulatory filing. Explain the mechanism first, briefly. MERC allows recovery of the annual fixed cost against a normative availability. Fall below it and a proportionate share of the fixed charge is disallowed. It is not a fine and it is not negotiable — it is arithmetic in the tariff order. Read the top three rows slowly, because these are the largest numbers of the day. Koradi Units 8-10 at 72.50 per cent against a norm of 85, carrying ₹28.04 crore. Chandrapur 3-7 at 64.88 against a lower norm of 80, carrying ₹23.94 crore. Khaperkheda 1-4 at 57.85, the lowest in the fleet, carrying ₹21.75 crore. Then point at the last row and let it sit. Parli Unit 8 ran at 97.40 per cent and carries nothing. The norm is achievable in this company, with this coal and these people. Land the connection. Every case in this block was about avoiding one forced outage. That is where this number comes from.

## Slide 50
What predictive maintenance needs from the organisation
The technical part is the smaller half — this is where programmes are actually won
3. Predictive maintenance
50
The alert-to-work-order loop
One named engineer owns triage, with a defined response time per criticality
Every alert carries its evidence — the signals, the residual and the trend — into the notification
A model alert becomes a CMMS notification, not an email that dies in an inbox
Every alert is closed with a finding: confirmed, not confirmed, or not inspected
Findings go back to the model owner monthly — that is the only way accuracy improves
Alert quality is reviewed as a number, the same way trip statistics are
What has to change around it
Spares policy — condition-based means the part is staged before the outage, not ordered after
Outage scope is built partly from model output, and something must come off the list in exchange
Instrumentation gaps are funded as part of the programme, not deferred to next year
Two trained people per station, so the programme survives a transfer
Contract and warranty terms updated where a vendor is doing the monitoring
A written rule that no model output enters protection or interlock logic
An alert that does not become a work order has cost you money and earned nothing. The loop is the programme.
Notes: [Slide 50 · 3. Predictive maintenance · target 12:52] [12:52–12:55] Slow this slide down. Everything before it was equipment. This is the part that decides whether any of it works. Read the left column as a sequence and stress the fourth item. Every alert closed with a finding — confirmed, not confirmed, or not inspected. That third option is deliberate and important, because pretending everything was inspected corrupts the record. Without honest closure you never learn whether the model is any good, and the programme quietly dies of unmeasured mistrust. On the right column, the spares point is the one that surprises managers. Predictive maintenance moves work earlier, which means the part must be available earlier. If procurement lead times are not addressed, a correct prediction produces a longer outage rather than a shorter one. The outage scope item needs saying plainly: if the model adds work, something must come off the list in exchange, otherwise the outage grows every cycle and the programme gets blamed. Land the last item on the right without softening it. No model output goes into protection or interlock logic. Ever.

## Slide 51
Why predictive maintenance programmes fail
Eight failures seen repeatedly across the industry, and what prevents each one
3. Predictive maintenance
51
WHY IT FAILED
WHAT PREVENTS IT
Trained on history that contained the fault
Check the training window against CMMS work orders first
Alerts went to an inbox nobody owned
One named triage engineer and a response time in writing
Too many alerts in the first fortnight
Start with three machines and tune persistence before more
No feedback on what the alert found
Close each alert: confirmed, not confirmed, or not inspected
Transmitter replaced, model never retrained
Instrument changes raise a model-review task automatically
Model output could not reach the work order
Build the historian-to-CMMS link inside the pilot, not after
Pilot proved value, nobody funded scale-up
Agree the scale-up trigger and budget before the pilot
The one engineer who understood it moved
Two trained people per station, plus written documentation
Not one of these eight is a modelling failure. Every one of them is an organisational failure, and every one is preventable.
Notes: [Slide 51 · 3. Predictive maintenance · target 12:55] [12:55–12:58] Three minutes, and the framing matters more than the detail. Open with the punch line rather than saving it: none of these eight failures is a mathematics problem. Every one is organisational, and every one is cheap to prevent if it is anticipated. Take row one seriously, because it is the most common and the most invisible. A model trained on a period that already contained the developing fault learns the fault as normal and never alerts. They saw exactly this in SIM-1 this morning. The countermeasure is simple and almost never done — check your training window against the CMMS work-order history before you train. Row three is the one that kills adoption fastest. Twenty alerts in the first fortnight and the operators stop reading them, permanently. Trust is spent once. Ask the room which of the eight they think is most likely at their own station. Their answers are useful intelligence for whoever writes the implementation plan, and they will be candid because none of it is hypothetical to them.

## Slide 52
Block close — four things to carry into lunch
Everything after the break is about our own numbers rather than equipment
3. Predictive maintenance
52
The residual, and then the trend
Monitoring says something has changed. Predictive maintenance fits a curve to that change and turns it into a date with a band around it.
One model per machine, never per unit
Per mill, per fan, per pump. A unit-level model averages six machines and hides precisely the one that is degrading.
An alert is not a work order
Nothing in this block earns a rupee until a named engineer triages it and the evidence reaches the CMMS with the notification.
₹100.87 crore
The cumulative fixed-charge disallowance for availability shortfall. That is what unavailability has already cost, before anybody buys anything.
After lunch we stop discussing equipment and start reading our own bill. Bring the same scepticism.
Notes: [Slide 52 · 3. Predictive maintenance · target 12:58] [12:58–13:00] Two minutes, no more. They are hungry and the afternoon is the important part of the day. Run the four cards briskly. The first is continuity from this morning: the residual detects, the trend projects. The second is the engineering rule they should apply to every proposal they see — one model per machine, never per unit. The third is the organisational rule from the previous slide, compressed to one line. The fourth card is the handover. Say it and then stop talking: one hundred crore and eighty-seven lakh, cumulative disallowance for availability shortfall, from our own June bill. Not an estimate, not a benchmark, not a vendor case study. Then set up the afternoon in one sentence. 'When we come back, every number on the screen comes out of MAHAGENCO's own regulatory filing for June 2026, and by the end of that block you will be able to read your own station's F10 sheet and say where your money is going.' Give them the return time clearly and let them go.

## Slide 53
4
SESSION · THE PIVOT OF THE DAY
Reading our own numbers
MAHAGENCO’s June 2026 regulatory filing, turned into an opportunity map
The decomposition: auxiliary power against boiler and turbine
What our fuel actually costs us, station by station
The merit order as a scoreboard
Where the ₹56 crore a month actually sits
14:30 – 15:00
30 minutes
Hands-on: SIM-2 — heat rate loss attribution
53
Notes: [Slide 53 · 4. Reading our own numbers · target 14:30] [14:30] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 54
Where this data comes from
Three documents this company already produces every month, and one that nobody reads
4. Reading our own numbers
54
The June 2026 energy bill
Bills 001/2026 and 35/2026. Station by station availability, PLF, gross and net generation. 4,588.47 MU sent out, ₹2,806.55 crore net.
The Part-I FSA bill and its F10 sheet
Provisional bill 43/2026, with the F10 energy charge rate calculation. Heat rate, auxiliary consumption, GCV, oil and transit loss, per station.
The MERC merit order stack
July 2026 revision zero, effective 16.07.2026 to 15.08.2026. Every station's variable charge and where it sits in the dispatch queue.
The document nobody reads
F10 is prepared for billing and then filed. It is the most complete performance record in the company, and it is not a performance report to anyone.
Nothing in this block is a benchmark, a vendor study or an assumption. It is our own filing, read as an engineering document.
Notes: [Slide 54 · 4. Reading our own numbers · target 14:30] [14:30–14:32] Two minutes. The only job of this slide is credibility, so do not linger. Say the framing sentence plainly: 'For the next half hour there is not one invented number on the screen. Everything comes from three documents this company produced in the last eight weeks.' Name them quickly. The energy bill gives availability, PLF and generation. The Part-I fuel surcharge bill carries the F10 energy charge rate calculation, which contains heat rate, auxiliary consumption, as-fired GCV, oil consumption and transit loss for every station. The merit order stack gives the variable charge and the dispatch rank. Spend the remaining time on the fourth card, because it is the point of the slide. F10 exists to compute a billing rate. It is prepared by the commercial department, submitted, and filed. Nobody in operations receives it as a performance report, and yet it is the most complete monthly statement of how each station actually ran. Ask the room directly: who here has seen their own station's F10 sheet? Usually one or two hands. That is the opportunity, before any technology is discussed.

## Slide 55
The fleet in one table, June 2026
Availability, PLF and net heat rate against MERC norm — eight groups chosen to show the spread
4. Reading our own numbers
55
Station | Avail % | PLF % | Net HR act / norm | Gap kcal/kWh
Nashik Units 3-5 | 94.62 | 58.40 | 2,804 / 2,754 | +50
Parli Unit 8 | 97.40 | 79.55 | 2,461 / 2,415 | +46
Khaperkheda Unit 5 | 87.86 | 82.03 | 2,385 / 2,375 | +10
Bhusawal Unit 6 | 79.01 | 70.37 | 2,183 / 2,139 | +44
Paras Units 3-4 | 74.83 | 66.92 | 2,578 / 2,415 | +163
Koradi Units 8-10 | 72.50 | 66.62 | 2,442 / 2,230 | +212
Chandrapur Units 3-7 | 64.88 | 53.56 | 2,709 / 2,688 | +21
Khaperkheda Units 1-4 | 57.85 | 54.55 | 2,715 / 2,630 | +85
₹56 crore
the net heat-rate gap against MERC norms across thirteen thermal groups, in June 2026 alone
Notes: [Slide 55 · 4. Reading our own numbers · target 14:32] [14:32–14:35] Three minutes. Let them find their own station first — say the row order is by availability, highest at the top, so they can locate themselves quickly. Draw out three contrasts and nothing more, or this becomes a reading exercise. First, availability and PLF are not the same thing. Nashik is the most available station in the fleet at 94.62 per cent and its PLF is 58.40. It is ready and it is not being called. Hold that thought — slide six explains why. Second, the heat-rate gap does not track the size or the age of the unit. Khaperkheda Unit 5 is ten kilocalories from its norm. Koradi Units 8-10, the newest and largest supercritical machines in the fleet, are two hundred and twelve away from theirs. Third, the norm itself differs. Comparing raw heat rates across rows is meaningless; the gap column is the only fair comparison, because each station is being judged against its own approved standard. The stat card is the number for the day. Fifty-six crore in one month, from heat rate alone. Roughly six hundred and seventy-six crore a year if June is typical.

## Slide 56
The decomposition that changes the conversation
One line of arithmetic that tells you whose problem the heat-rate gap actually is
4. Reading our own numbers
56
THE IDENTITY
Gross HR = net HR × (1 − aux fraction)
Every station already reports a net heat rate and an auxiliary consumption percentage. Multiply one by one minus the other and you have the gross heat rate — what the boiler and turbine actually achieved. MERC publishes a norm for both. Almost nobody in the plant does this arithmetic.
WHAT IT REVEALS
A combustion problem, or an electrical one
The net gap splits into two pieces with two different owners and two entirely different remedies. A positive gross gap is combustion, condenser and air pre-heater. A negative gross gap means the plant is beating its norm and every kilocalorie of the penalty is electricity consumed inside the fence.
Nashik's gross heat rate is 2,440 against a normative 2,458 — the boiler and turbine are beating the norm by 18 kcal/kWh, and the entire 50 kcal/kWh penalty is auxiliary power at 12.96 % against 10.75 %.
Notes: [Slide 56 · 4. Reading our own numbers · target 14:35] [14:35–14:38] This is the pivot of the afternoon. Slow down and let the arithmetic land before you show the result. Write the identity in the air as you say it: gross heat rate equals net heat rate multiplied by one minus the auxiliary fraction. Then say why it matters. Net heat rate already contains auxiliary power inside it. So a station can be penalised on net heat rate while its boiler and turbine are performing better than the norm, and the raw number gives no hint of that at all. Now deliver the Nashik result and pause. Gross 2,440 against a normative 2,458. The boiler and the turbine are seventeen kilocalories better than the standard MERC set for them. Every one of the fifty kilocalories of penalty is auxiliary power, at 12.96 per cent against a norm of 10.75. Say what that changes. A combustion optimisation project at Nashik would be aimed at the one part of the station that is already winning. The money is in the switchgear. Ask the room whether anybody has ever seen this split for their own station.

## Slide 57
Station by station — where the gap actually sits
The same net gap, decomposed. A negative gross gap means the plant is beating its norm.
4. Reading our own numbers
57
Station | Aux gap pp | Gross HR act / norm | Gross gap | Diagnosis
Chandrapur Units 3-7 | +3.02 | 2,393 / 2,455 | −62 | Auxiliary power is the whole problem
Nashik Units 3-5 | +2.21 | 2,440 / 2,458 | −18 | Auxiliary power is the whole problem
Parli Unit 8 | +2.24 | 2,197 / 2,210 | −13 | Auxiliary power is the whole problem
Khaperkheda Unit 5 | +0.57 | 2,228 / 2,232 | −5 | Auxiliary power is the whole problem
Khaperkheda Units 1-4 | +2.74 | 2,377 / 2,375 | +2 | Both, roughly balanced
Koradi Unit 6 | +0.56 | 2,246 / 2,190 | +56 | Mostly boiler and turbine
Paras Units 3-4 | +2.29 | 2,279 / 2,190 | +89 | Mostly boiler and turbine
Koradi Units 8-10 | +0.95 | 2,272 / 2,096 | +176 | Mostly boiler and turbine
₹22.84 crore
Koradi 8-10's GROSS gap: 176 kcal/kWh on 964.8 MU generated. Its NET gap of 212 on 897.75 MU sent out is worth ₹25.61 crore. Same station, two questions — and mixing them is the error this whole session is about
Notes: [Slide 57 · 4. Reading our own numbers · target 14:38] [14:38–14:40] Two minutes, and it is a pointing slide rather than a reading slide. Give them the top four rows and the bottom row. The top four all have a negative gross gap. Four station groups whose boilers and turbines are better than the standard MERC approved for them, and which are nonetheless being penalised on net heat rate. Chandrapur Units 3-7 are sixty-two kilocalories better than their gross norm and carry a three point zero two percentage point auxiliary gap. Every rupee of their heat-rate penalty is electricity consumed inside the fence. Now the bottom row, which is the opposite case. Koradi Units 8-10 have almost no auxiliary gap at nought point nine five, and a genuine one hundred and seventy-six kilocalorie boiler and turbine gap on 964.8 MU. That is combustion, condenser and air pre-heater work, and it is worth ₹22.84 crore in one month by itself — that is the gross gap valued on gross generation. One housekeeping note if anyone is sharp: the minus eighteen for Nashik here and the seventeen quoted on the previous slide are the same figure at two different roundings. Same table, two opposite programmes. That is why the decomposition comes before the project list. Watch the stat card, and say this out loud, because it is the discipline the whole session is teaching: the gross gap is 176 kcal/kWh and it is valued on the 964.8 MU the station generated, giving ₹22.84 crore. The net gap is 212 and it is valued on the 897.75 MU it sent out, giving ₹25.61 crore. Both are correct. Multiplying a gross gap by net units, or the reverse, is exactly the mistake that produces the ₹89 crore number nobody can defend.

## Slide 58
What our fuel actually costs us
Cost of heat = MOD variable charge ÷ net heat rate. The station's own money, not an assumption.
4. Reading our own numbers
58
Station | MOD variable charge ₹/kWh | Net heat rate kcal/kWh | Cost of heat ₹/kcal | Implied as-fired coal ₹/tonne
Nashik Units 3-5 | 5.9800 | 2,804 | 0.002133 | 6,217
Bhusawal Unit 3 | 4.9470 | 2,848 | 0.001737 | 5,280
Koradi Units 8-10 | 3.2840 | 2,442 | 0.001345 | 4,116
Khaperkheda Unit 5 | 3.1890 | 2,385 | 0.001337 | 3,655
70 %
spread in implied as-fired coal cost between Khaperkheda Unit 5 and Nashik, inside one company
Indicative basis
Cost of heat = each station's own MERC merit-order variable charge divided by its own actual net heat rate for June 2026. Implied coal cost = cost of heat × as-fired GCV. These are the station's own figures, not an assumption.
Nashik's coal costs ₹6,217 a tonne against ₹3,655 at Khaperkheda 5 — nearly twice. The same kcal/kWh saved is worth far more at Nashik.
Notes: [Slide 58 · 4. Reading our own numbers · target 14:40] [14:40–14:42] Two minutes. This slide gives every station in the room its own price for a kilocalorie, and that price should decide where effort goes. Explain the arithmetic in one line. Divide the station's own merit order variable charge by its own actual net heat rate and you have the cost of one kilocalorie of delivered heat. No assumed coal price, no assumed GCV, no benchmark. Work back through the as-fired GCV and you get the implied delivered cost of a tonne of coal. Then read the two ends. Nashik at ₹0.002133 a kilocalorie and an implied ₹6,217 a tonne. Khaperkheda Unit 5 at ₹0.001337 and ₹3,655. Seventy per cent apart, inside one company, in one month. Draw the consequence out loud. Ten kilocalories per kilowatt hour saved at Nashik is worth substantially more than the same ten at Khaperkheda 5, on the same generation. Efficiency effort should follow the cost of heat, not the size of the unit or the age of the plant. Ask each station to note its own row from the handout before we move on.

## Slide 59
The merit order is a scoreboard
How heat rate and coal cost decide whether a station that is ready actually gets called
4. Reading our own numbers
59
₹5.98 per kWh
Nashik's July 2026 variable charge. The most expensive coal station in the MSEDCL stack, ranked tenth overall and behind only gas.
94.62 per cent available
The highest availability in the fleet. The plant is ready, declared and staffed. Availability is not the constraint here.
58.40 per cent PLF
And it is not being called. The gap between those two numbers is the merit order doing exactly what it is designed to do.
The causal chain
Heat rate and coal cost set the variable charge. The variable charge sets the rank. The rank sets the PLF. The PLF sets fixed-cost recovery.
Where the lever is
Rank is relative and nobody controls the other bidders. The only lever inside the fence is the station's own variable charge.
This is structural, not blame
1979 to 1981 vintage units on the most expensive coal in the fleet. The mechanism is arithmetic, and it is worth understanding rather than resenting.
Every kilocalorie per kilowatt hour and every rupee per tonne moves you up or down a ranked list that decides whether you run at all.
Notes: [Slide 59 · 4. Reading our own numbers · target 14:42] [14:42–14:44] Handle this slide carefully. Nashik is the host station and several people in the room work there, so make the framing structural from the first sentence. Say it directly: 'This is not a criticism of anybody's operation. It is how the merit order works, and Nashik happens to be the clearest illustration in the fleet.' Then walk the chain slowly, because it is the most important causal argument of the day. Heat rate and delivered coal cost together set the variable charge. The variable charge sets the position in the merit order. The position determines how much the station is despatched. Despatch determines PLF. And PLF determines how well the fixed cost is recovered. Hold the two Nashik numbers side by side. Highest availability in the fleet at 94.62 per cent, PLF at 58.40. The station is ready and the stack is not calling it. Make the honest point about the lever. Nobody at a station controls where the other generators bid. What a station controls is its own variable charge, and that is heat rate and fuel cost — the two things this block has just decomposed.

## Slide 60
The auxiliary power bill
Electricity generated and then consumed inside the fence, above the approved norm
4. Reading our own numbers
60
Station | Aux actual % | Aux norm % | Excess MU/month | Value ₹ cr/month
Chandrapur Units 3-7 | 11.69 | 8.67 | 23.03 | 9.52
Nashik Units 3-5 | 12.96 | 10.75 | 5.85 | 3.50
Khaperkheda Units 1-4 | 12.44 | 9.70 | 9.38 | 3.42
Parli Units 6-7 | 12.41 | 9.30 | 7.86 | 3.25
Koradi Units 8-10 | 6.95 | 6.00 | 9.17 | 3.01
Bhusawal Units 4-5 | 7.06 | 6.00 | 5.85 | 2.37
Paras Units 3-4 | 11.59 | 9.30 | 5.61 | 2.22
Parli Unit 8 | 10.74 | 8.50 | 3.26 | 1.35
81.5 MU
above norm in one month, worth ₹32.9 crore — a component of the ₹56 crore, never an addition to it
Notes: [Slide 60 · 4. Reading our own numbers · target 14:44] [14:44–14:47] Three minutes, and one warning that must not be skipped. Give them the scale first. Eighty-one and a half million units above normative auxiliary consumption in a single month. That is roughly the monthly output of a small unit, generated and then consumed inside the fence. Valued at each station's own variable charge it is ₹32.9 crore. Read the worst three: Parli Units 6-7 at 12.41 against a norm of 9.30, Chandrapur 3-7 at 11.69 against 8.67, Nashik at 12.96 against 10.75. Note that Chandrapur 3-7 carries the largest excess in absolute terms at 23.03 MU because of its size, and the largest value at ₹9.52 crore. Now the warning, and say it slowly. This ₹32.9 crore is not additional to the ₹56 crore heat-rate gap. Net heat rate already contains auxiliary power. The auxiliary figure is a component of the fifty-six, not an addition to it. Any business case that adds them together double counts about thirty-three crore and will not survive its first meeting with finance. Ask them to write that down. It is the most common error in this arithmetic.

## Slide 61
The oil and the coal
Two costs that sit outside the heat-rate arithmetic and are measured every single day
4. Reading our own numbers
61
Secondary fuel oil — burning oil to hold a flame
Chandrapur Units 3-7: 3.23 ml/kWh against a normative 1.00
Parli Units 6-7: 2.87 ml/kWh against a normative 0.50 — nearly six times
Oil support is a symptom of low-load running and flame-stability anxiety
It is the most expensive heat in the station, by a wide margin
Much of it is precautionary rather than necessary, and nobody measures which
Coal quality — what arrives is not what was bought
GCV loss between loading and unloading: 619 to 941 kcal/kg
As-fired GCV across the fleet: 2,733 to 3,270 kcal/kg
Paras transit loss 1.924 % against a normative 0.800 %
Stacking loss taken at 85 kcal/kg at every station
Six stations blend imported coal at 4,624 to 4,709 kcal/kg as fired
Both columns are measured daily and analysed monthly at best. Both are prediction problems long before they are procurement problems.
Notes: [Slide 61 · 4. Reading our own numbers · target 14:47] [14:47–14:49] Two minutes on the two costs that sit outside the heat-rate arithmetic and are usually treated as somebody else's department. On oil, give the comparison rather than the raw figure. Parli Units 6-7 at 2.87 millilitres per kilowatt hour against a norm of 0.50 is nearly six times the allowance. Chandrapur 3-7 at 3.23 against 1.00. Then ask the question that matters: how much of that oil was genuinely required to hold a flame, and how much was precautionary because nobody could be sure. Nobody in any station can answer that today, and that is exactly what a flame-stability prediction addresses. On coal, the transit loss and GCV loss figures are the ones to stress. Six hundred and nineteen to nine hundred and forty-one kilocalories per kilogram lost between loading and unloading. Paras at 1.924 per cent transit loss against a norm of 0.800. Make the connection to this morning. A GCV soft sensor predicts as-fired quality from plant signals hours before the laboratory result arrives. That is SIM-4, and it is a supervised model trained on your own lab data.

## Slide 62
Lab — SIM-2 · Heat rate loss attribution
Ten minutes at the keyboard, on your own station's June 2026 numbers
4. Reading our own numbers
62
SIM-2
Heat rate loss attribution
10 minutes at your laptop
Do this
Open SIM-2 and select your own station from the dropdown. Read the facts panel underneath it.
Read the split: how much of your net heat-rate gap is auxiliary power, and how much is boiler and turbine.
Select Nashik Units 3-5, then Koradi Units 8-10. Same question, opposite answers.
Go back to your own station and move the controllable-parameter sliders — excess oxygen, main steam temperature, back pressure, unburnt carbon, air pre-heater leakage.
Drag the auxiliary power reduction slider and see what closing half a percentage point is worth at your own variable charge.
Read the red warning at the bottom of the module before you close it.
Watch for
For Nashik the boiler and turbine bar sits below the line — better than the norm. The whole gap is the auxiliary bar.
Koradi Units 8-10 are the mirror image: a 176 kcal/kWh plant gap and almost no auxiliary gap at all.
The fleet chart shows four station groups with negative bars — four whose plant is beating its own norm.
Every slider move changes the monthly rupee figure immediately, priced at that station's own variable charge.
Two stations, the same penalty on paper, and opposite remedies. The decomposition decides which project is worth funding, and it takes one line of arithmetic on data the commercial department already files every month.
Notes: [Slide 62 · 4. Reading our own numbers · target 14:49] [14:49–14:59] [LAB] Ten minutes, and this is the lab that most directly changes what people do on Monday. Get them started fast. Frame it in one sentence: 'This module is running on the June 2026 F10 figures for your own station. The decomposition is the identity from three slides ago, and the rupee arithmetic uses your own merit order variable charge.' Insist on move three, because it is the teaching point. Nashik and then Koradi Units 8-10, one after the other. Two stations with a similar-looking net penalty and completely opposite diagnoses. Ask somebody from each station to say aloud what their own bar chart shows. Walk the room during moves four and five. The auxiliary slider is where the room usually goes quiet, because half a percentage point turns out to be worth more than most people assume. Move six is not optional. The red panel is the warning that the fifty-six crore and the thirty-three crore are not additive. Reconvene at fourteen fifty-nine sharp. Take one sentence from two different stations before the last slide.

## Slide 63
The opportunity map
Five pain points from our own June 2026 filing, each with its evidence and an honest confidence rating
4. Reading our own numbers
63
1 · Availability — ₹100.87 cr disallowed · worst Koradi 8-10
Predictive maintenance and early-warning anomaly detection on the plant driving forced outages; outage scope built from model output
Proven — anomaly detection is the safest first project in any station
2 · Auxiliary power — 81.5 MU, ₹32.9 cr · worst Chandrapur 3-7
Combinatorial optimisation of mill, fan and CW pump combinations plus ESP field energisation, offered as operator advice
Proven as advisory — the gain depends on how well you already schedule
3 · Boiler and turbine — 176 kcal/kWh · worst Koradi 8-10
Combustion optimisation with online loss attribution, plus condenser and air pre-heater analytics feeding a daily loss report
Emerging — proven as advice, closed loop needs full engineering controls
4 · Secondary fuel oil — 3.23 ml/kWh · worst Chandrapur 3-7
Flame-stability prediction to avoid precautionary oil support at low load, and start-up sequence optimisation
Emerging — depends on flame scanner and mill data you may not historise
5 · Coal quality — GCV loss 619 to 941 kcal/kg · worst Paras
GCV soft sensor trained on your own laboratory results, rake-level transit-loss analytics and blend optimisation
Proven as a soft sensor — but the error must be reported honestly
These are the values of closing each gap entirely against norm. No programme closes a gap entirely. Fifteen to twenty-five per cent of the identified gap is a defensible first-year planning assumption.
Notes: [Slide 63 · 4. Reading our own numbers · target 14:59] [14:59–15:00] One minute. This is the slide people will photograph, so give it the time it needs and end on the punch line rather than on a summary. Run down the first column only, naming the pain point and its evidence, and let the second and third columns be read rather than spoken. Availability first, because the ₹100.87 crore disallowance is the largest single number in our own filing. Auxiliary power second at 81.5 MU and ₹32.9 crore. Boiler and turbine third, concentrated almost entirely at Koradi Units 8-10. Oil fourth, coal quality fifth. Then stop and read the punch line word for word, slowly. Every rupee figure on this map is the value of closing a gap completely against the norm. No programme in any industry closes a gap completely. Fifteen to twenty-five per cent of the identified gap in the first year is what a serious plan assumes, and anybody promising more should be asked for their evidence. Say the last sentence and leave it there: this map came out of our own bill, not out of a brochure.

## Slide 64
5
SESSION
What other generators have done
NTPC, Tata Power, Coal India, SAIL — and Vistra and Duke Energy internationally
Indian public-sector and private deployments, named
Vistra: 67 units, 1 per cent, US$ 23 million
Duke Energy: the operating model worth copying
Reading a vendor claim without being taken in
15:00 – 15:12
12 minutes
64
Notes: [Slide 64 · 5. What others have done · target 15:00] [15:00] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 65
What other generators have actually done
Named companies, named systems — and where the numbers are verified against where they are vendor claims
5. What others have done
65
NTPC — NePPS
NETRA e-Power Plant Solutions: an AI-based operator advisory system predicting equipment faults from sensor data, developed at NTPC's NETRA research centre and Advanced Computing Center.
Tata Power — enterprise data platform
Announced April 2026 with Databricks: a unified data and AI platform across a 16 GW+ portfolio. Grid management, renewable forecasting and a 'talk-to-data' agent. Note honestly: thermal generation is not named in the announcement.
Adani Electricity — Mumbai distribution
AspenTech deployment supporting reliable supply to about three million customers. Distribution, not generation — but the same asset-analytics family.
Coal India — the fuel end
AI satellite dashboard with ISRO's National Remote Sensing Centre for underground coal fires at Jharia and Dhanbad; over 500 AI surveillance cameras; a 'Digi Coal' platform with 17 AI use cases.
SAIL Bokaro — adjacent heavy industry
AI-assisted stoichiometric optimisation reported at ₹3.23 crore annual savings and 1,500 tonnes of CO₂ avoided. A combustion-chemistry optimisation, in a PSU, in India.
NLC India and NPCIL
Memoranda of understanding with IIT Kanpur and IIT Bombay respectively for AI and machine learning capability building. The academic-partnership route, which a state utility can copy directly.
Every one of these is a public-sector or Indian private generator. None of this is a Western experiment.
Notes: [Slide 65 · 5. What others have done · target 15:00] [15:00–15:03] The point of this slide is not vendor promotion. It is to remove the objection that this is something foreign companies do. Start with NTPC — NePPS is the closest analogue to what MAHAGENCO would build, and it came out of their own research centre rather than a purchase. Be scrupulously honest about Tata Power: the Databricks announcement is about grid, renewables and customer data. Thermal generation is not mentioned. Say that out loud. If you overstate one reference, the room will discount all six. The SAIL Bokaro number is the most useful one for a sceptic — ₹3.23 crore a year from optimising combustion chemistry, in an Indian PSU, reported publicly. Ask the room: 'Which of these six is closest to something you could start at your station in ninety days?' The honest answer is usually the NLC and NPCIL route — a partnership with an engineering institute.

## Slide 66
Vistra — the case that maps onto our problem exactly
A US thermal generator, a heat-rate optimiser, and a fleet rollout with published numbers
5. What others have done
66
Stage | What was done | Result | Note
Pilot — Martin Lake, Texas | Multi-layered neural network heat-rate optimiser recommending setpoints every 30 minutes, built by McKinsey and QuantumBlack | 2 % heat rate improvement in three months | Model prediction accuracy reported at 99 % or better
Pilot value | Same plant, annualised | US$ 4.5 million a year; 340,000 tonnes of CO₂ abated | One plant
Fleet rollout | 67 generating units across 26 plants | 1 % average efficiency improvement | The fleet average is half the pilot — that is the honest pattern
Fleet value | Company-wide | US$ 23 million; 1.6 million tonnes of CO₂ avoided | Published by the company and its consultants
1 % → 24 kcal/kWh
the fleet-average result applied to Koradi 8-10's actual 2,442 kcal/kWh — against a gap of 212
Notes: [Slide 66 · 5. What others have done · target 15:03] [15:03–15:07] This is the single most useful external reference in the day, because it is the same problem we looked at ten minutes ago. Walk the four rows. Then do the arithmetic aloud: one per cent of Koradi 8-10's actual net heat rate of 2,442 kcal/kWh is about 24 kcal/kWh. Their measured gap against norm is 212. So a Vistra-class result would recover roughly a ninth of the identified gap — which at Koradi's own cost of heat is still meaningful money. Make the honest point about the third row: the pilot got 2 per cent, the fleet averaged 1 per cent. That halving is completely typical, and any business case that assumes the pilot number will replicate across the fleet is wrong. Plan on the fleet number. Ask: 'What would it take for us to run a thirty-minute setpoint advisory on one unit?' The answer is Session 5.

## Slide 67
Duke Energy — the operating model worth copying
Not the algorithm. The monitoring and diagnostics centre around it.
5. What others have done
67
Element | Duke Energy | What it means for a five-station fleet
Coverage | Over 87 % of the generating fleet — about 58,000 MW across seven states | Fleet-wide, not one flagship unit
Scale of models | Over 11,000 models drawing on more than 500,000 data points | One model per machine, not one model per plant
The team | A central monitoring and diagnostics centre staffed by five analysts | Five people watching a fleet — the economics only work centrally
The result | A single early catch reported as avoiding over US$ 34 million in 2016 | One catch paid for the programme many times over
Their competitive advantage is not the software. It is that five named people look at the alerts every single day.
Notes: [Slide 67 · 5. What others have done · target 15:07] [15:07–15:10] Duke Energy runs AVEVA's PRiSM predictive asset analytics. The technology matters less than the structure around it, and that structure is directly copyable. Dwell on the third row. Five analysts. Eleven thousand models. That ratio only works because the monitoring is centralised — no station can justify a dedicated analyst, but a fleet can. MAHAGENCO has thirteen thermal unit groups across seven stations. A central monitoring cell of three to five engineers, seeing every station's alerts, is a realistic organisational proposal and it is the one thing on this slide you could put in a note to management next week. The US$ 34 million single catch is the headline, but be careful with it — it is one event, in one year, reported by the vendor. Use it as an existence proof of the upside, not as an expected value.

## Slide 68
Adani Power — the Indian case, and what it does not tell us
AVEVA World, Paris, October 2024 — their own slides, their own screenshots
5. What others have done
68
What they showed | The detail | Evidence
Scope | AVEVA PI System across 8 thermal locations, 25 units, about 150,000 tags, one central operations centre at Ahmedabad. Udupi (1,200 MW) is one of the eight. | Their own conference slides
Boiler and turbine efficiency | Every loss itemised on screen on a 15-minute AND a 24-hour window. Live screenshot: boiler efficiency 86.72 % last 15 min against 86.49 % last 24 h; turbine heat rate 1,883 against 1,826 design. | Screenshots, dated
Asset Health Index | Four tiers — station, asset, equipment, sensor. Pumps 69, fans 71, mills 77. Individual BFP, CEP and CWP scored. Motor winding and motor bearing temperature are scored inputs. | Screenshots, dated
Is it AI? | The 15-minute efficiency is a thermodynamic enthalpy–entropy module in PI Asset Framework, with coal quality typed in by hand. The AI/ML is Python health scoring. Predictive analytics was still on the roadmap. | Stated on their slides
The published benefit | None. Not a kcal/kWh, not a percentage point of availability, not a rupee. Their own annual report quantifies heat-rate gains only for air-preheater baskets and water-box cleaning — the mechanical work, not the software. | Nothing found
Well-documented capability. Undocumented benefit. Learn to tell those two apart and you can read any vendor case study in this industry.
Notes: [Slide 68 · 5. What others have done · target 15:05] [15:05–15:10] Five minutes, and this is the most useful slide in the block for a MAHAGENCO audience, because it is the nearest neighbour — an Indian state-scale thermal fleet, imported and domestic coal, the same auxiliaries. Give them the good news first, because it is genuinely impressive and it is real. Eight sites, twenty-five units, a hundred and fifty thousand tags, one operations centre in Ahmedabad. Boiler losses itemised every fifteen minutes. A health index that scores your boiler feed pumps individually. This is not a pilot on one unit, it is a fleet. Then the two corrections, and take your time over them. First: the fifteen-minute efficiency calculation is NOT machine learning. It is thermodynamics — enthalpy and entropy in PI Asset Framework — with coal quality entered manually. That is a heat balance running continuously, which is a fine thing and something we could do, but it is not AI, and their own slide says so. The AI/ML in that deployment is Python code scoring health parameters. Second, and this is the one to sit on: there is no published number. Not in the vendor deck, not on AVEVA's website, not in Adani Power's own annual report. In that annual report the only two heat-rate improvements quantified in kilocalories are credited to replacing air-preheater baskets and cleaning water boxes. The digital programme is listed with no number attached at all. So the honest reading is: capability documented, benefit undocumented. That is not an accusation — it is the normal state of this industry's published evidence, and NTPC's PI System presentation has exactly the same shape. If somebody asks for an Indian number they can actually stand behind, give them NTPC Talcher Kaniha: station heat rate 2,700 down to 2,614 kcal/kWh over five years, USD 35 million saved, verified under ISO 50001 and the BEE PAT scheme and audited by the CAG. Even there the savings are not decomposed to say what the software contributed. That is how thin the ground is, and it is why we spent this morning on measurement.

## Slide 69
Reading vendor claims without being taken in
The weak end of the same list. The three cases above came with named plants and published numbers; these do not.
5. What others have done
69
Adani Power AVEVA PI programme
8 sites, 25 units, 150,000 tags, live screens — and no published benefit figure anywhere, including their own annual report
Proven as deployed; benefit unquantified publicly
NTPC NePPS operator advisory
Named system, named research centre, no published benefit figure
Proven as deployed; benefit unquantified publicly
GE Vernova performance software
'Up to 1 % heat rate reduction in 12 months'; customer examples anonymous
Emerging — vendor claim, no named plant
Tata Power enterprise AI platform
Announced April 2026; grid and renewables, thermal not named
Emerging — a platform announcement, not a result
Generic 'AI saves 10–15 %' marketing
No plant, no baseline, no measurement method
Experimental — treat as advertising until a baseline appears
Three questions for any vendor: which plant, what baseline, and who measured it? If any answer is missing, the number is marketing.
Notes: [Slide 69 · 5. What others have done · target 15:10] [15:10–15:12] This slide is the most practically useful of the block, because everyone here will sit through vendor presentations in the next year. Give them the three questions and make them write them down: which plant, what baseline, who measured it. A claim that survives all three is worth engaging with. A claim that fails any one of them is advertising. Point out that even the strong references have caveats. Vistra's fleet number is half its pilot number. Duke's US$ 34 million is a single event. NTPC's system is real but publishes no benefit figure. Being able to state the caveat is what makes you credible when you take a proposal to management. End with the honest position: the technology is proven, the benefit is real and smaller than the brochure, and the variable that decides your outcome is your own data and your own follow-through.

## Slide 70
What the evidence actually supports
Setting an expectation you can defend in a review meeting
5. What others have done
70
WHAT THE BROCHURES SAY
5 to 15 per cent
Efficiency gains, availability improvements and cost reductions quoted without a named plant, a stated baseline or an independent measurement. Almost always a pilot result on a poorly tuned unit, annualised and generalised.
WHAT THE PUBLISHED FLEET RESULTS SAY
About 1 per cent
Vistra's 67-unit rollout averaged 1 per cent against a 2 per cent pilot. GE Vernova claims up to 1 per cent in twelve months. On MAHAGENCO's June 2026 thermal generation, 1 per cent of heat rate is roughly 24 kcal/kWh on a 2,400 kcal/kWh unit — real money, and nothing like the brochure.
Plan on the fleet number, not the pilot number. A business case built on 10 per cent will be shredded, and it will take the credible 1 per cent down with it.
Notes: [Slide 70 · 5. What others have done · target 15:11] [15:11–15:12] Close the block on expectation management, because this is where internal credibility is won or lost. The sentence that matters is the punch line. If someone in this room takes a proposal to a director claiming ten per cent and delivers one, the next five proposals from this room will not be read. Relate it back to Session 4: our identified gap is 212 kcal/kWh at Koradi 8-10. A Vistra-class outcome recovers around 24 of that. That is not a disappointment — it is ₹2.95 crore a MONTH at that station's own cost of heat — about ₹35 crore a year, from software and discipline rather than capital works. Then move straight into Session 5, which is how that 24 kcal/kWh is actually earned.

## Slide 71
6
SESSION
Operation and performance optimisation
Combustion, condenser, auxiliary power and coal quality — where the kcal/kWh actually come from
The controllable-loss table, and online loss accounting
Combustion optimisation and the engineering that makes it safe
Auxiliary power as a scheduling problem
How a soft sensor is built
15:12 – 15:45
33 minutes
Hands-on: SIM-6 and SIM-3
71
Notes: [Slide 71 · 6. Performance optimisation · target 15:12] [15:12] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 72
The controllable loss table
Indicative heat-rate sensitivities — subcritical against supercritical, and who can actually move each one
6. Performance optimisation
72
Parameter | Deviation from design | Subcritical 210–500 MW | Supercritical 660 MW | Who influences it daily
Boiler efficiency | 1 % drop | ≈ 30 kcal/kWh | ≈ 25 kcal/kWh | Operations and combustion
Main steam temperature | 10 °C below design | 5–8 kcal/kWh | 4–6 kcal/kWh | Operations
Reheat steam temperature | 10 °C below design | 4–6 kcal/kWh | 4–5 kcal/kWh | Operations
Condenser back pressure | 10 mmHg rise | 8–12 kcal/kWh | 7–10 kcal/kWh | Mechanical and chemistry
Excess O₂ | 1 % above optimum | 10–15 kcal/kWh | 8–12 kcal/kWh | Operations, every shift
Unburnt carbon in ash | 1 % increase | 10–15 kcal/kWh | 10–15 kcal/kWh | Mills and combustion
Final feedwater temperature | 5 °C below design | 4–6 kcal/kWh | 4–6 kcal/kWh | Heaters and mechanical
APH air leakage | 5 % increase | 3–5 kcal/kWh, plus ID fan power | 3–5 kcal/kWh, plus ID fan power | Maintenance
₹14–44 lakh a year
what one kcal/kWh is worth on a 210 to 660 MW unit — indicative, at 65 per cent PLF
Notes: [Slide 72 · 6. Performance optimisation · target 15:12] [15:00–15:02] Open the money block with this table up and do not rush it. Say plainly that these sensitivities are indicative and typical, not measured at your station. Every unit has its own numbers and the OEM heat balance is where they live. What is not indicative is the shape of the table: the two largest single items are excess O₂ and unburnt carbon, and both are influenced by an operator on every shift. Point at the supercritical column and make the comparison explicit. A 660 MW supercritical unit is less sensitive in kcal/kWh terms simply because its base heat rate is lower — but the same percentage loss on a bigger machine is more coal. Ask the room directly: which of these eight does your station measure well enough to act on today, and which do you only ever see in the monthly performance report? The honest answer for most stations is two or three. Land it on the stat card. One kcal/kWh held for a year is fourteen to forty-four lakh rupees depending on unit size. Across the thirteen groups, the June 2026 net heat-rate gap was fifty-six crore rupees in a single month. This table is the anatomy of that number.

## Slide 73
Online loss accounting
What an expected-heat-rate model does that a monthly spreadsheet cannot
6. Performance optimisation
73
THE MONTHLY PERFORMANCE REPORT
One number, four weeks late
It tells you the unit ran at 2,425 kcal/kWh against 2,375 normative. It cannot tell you which shift, which coal, which mill combination or which fouled surface produced the gap — because by the time it is compiled, every one of those conditions has gone.
AN EXPECTED-HEAT-RATE MODEL
A deviation, attributed, now
It computes every few minutes the heat rate this unit should be achieving at this load, this coal, this ambient and this cooling water temperature, then splits the gap across back pressure, excess air, unburnt carbon, feedwater temperature and auxiliary power while the shift is still running.
A monthly report tells you that you lost the money. An online loss account tells you where it went, and who is still in a position to stop it.
Notes: [Slide 73 · 6. Performance optimisation · target 15:14] [15:02–15:04] Two minutes. This is the bridge from the sensitivity table to everything that follows. The left panel is not a criticism of the performance engineer. The monthly report is a correct calculation of a dead month. Say it that way — the arithmetic is right, the timing makes it useless for control. Explain expected heat rate in one sentence: the same idea as the residual from this morning, applied to the whole unit instead of one bearing. Given load, coal, ambient and cooling water temperature, the unit should be at a certain heat rate. It is at another. The difference is the only number worth managing. The attribution is the part that changes behaviour. A gap of fifty kcal/kWh means nothing to a shift engineer. Fifty kcal/kWh of which twenty-three is auxiliary power, eleven is back pressure and nine is excess air — that is four separate conversations with four different people, and three of them can act before the shift ends. Ask the room: how long after a heat-rate excursion does your station currently find out? Let the answer sit before moving on.

## Slide 74
Combustion optimisation — what it actually does
And what has to be engineered around it before it goes anywhere near the DCS
6. Performance optimisation
74
What the system does
Learns a boiler model from your own operating data, not from a design manual
Searches combinations of excess O₂, burner tilt and secondary air damper positions
Brings mill combination and over-fire air into the same search
Writes small bias values to the DCS — it nudges setpoints, it does not replace the control loops
Re-optimises as coal, load and equipment condition change through the shift
States the predicted gain in kcal/kWh before anything is allowed to move
What honest engineering requires
Hard clamps on every variable it is permitted to touch
Rate limits, so nothing moves faster than the boiler can follow
A watchdog that returns the unit to base control if the optimiser stops responding
Bumpless transfer in and out, tested in both directions
Operator override on one button, available at all times, no password
Availability above 90 per cent in service before anyone believes the reported benefit
Vendors sell the left column. Your commissioning engineer has to build the right one — and the right one decides whether the benefit still exists in year two.
Notes: [Slide 74 · 6. Performance optimisation · target 15:16] [15:04–15:06] Two minutes, and give the right column more of them than the left. The left column is genuinely unremarkable engineering: a model fitted to your own data, a search over a handful of manipulated variables, a bias written to the DCS. Say the word bias carefully — it moves an existing setpoint within a bound. It does not take over the control loop and it does not touch a protection. The right column is where these projects live or die. Read the availability line aloud and dwell on it: if the optimiser is in service forty per cent of the time, the benefit reported in the contract is a benefit nobody received. Ask the room whether anyone has an advanced control application on their unit that is currently switched off. There will be hands, and there always are. The honest line to say: every one of the right-hand items is unglamorous, none of it appears in the sales presentation, and all of it is your responsibility to specify before the purchase order goes out. Set up the next slide by asking what the optimiser is optimising for. Nobody ever asks.

## Slide 75
The trade-off nobody puts on the brochure
NOx, unburnt carbon, heat rate and CO move against each other — always
6. Performance optimisation
75
NOx
Lower excess air and staged combustion bring NOx down. The same moves push unburnt carbon up and can cost flame stability at low load.
Unburnt carbon
Each 1 per cent increase costs an indicative 10 to 15 kcal/kWh and downgrades the ash. Raise O₂ to fix it and you pay in NOx and dry gas loss.
Heat rate
The best O₂ for heat rate sits above the best O₂ for NOx and below the point where CO breaks away. It is a narrow window and it moves with coal.
CO and slagging
Rising CO is the boiler saying the window has closed. Slagging and high furnace exit gas temperature are the slower, more expensive version of the same message.
The weights in that objective function are a management decision, not a technical one. Somebody senior has to sign what a milligram of NOx is worth in kcal/kWh.
Notes: [Slide 75 · 6. Performance optimisation · target 15:18] [15:06–15:08] Two minutes, and make this the slide they argue about. Walk the four cards quickly, then stop on the punch line and stay there. Every combustion optimiser contains a weighted sum. Somebody chose those weights. In almost every installation that somebody was a commissioning engineer under time pressure, working alone, and nobody in the station has looked at the numbers since. Put the question to the room in its uncomfortable form: what is one milligram per normal cubic metre of NOx worth to MAHAGENCO in kcal/kWh? Nobody can answer it, and that is exactly the point. It is a policy question about emission compliance margin against fuel cost, and it belongs to management, not to the algorithm. Say the consequence plainly. If you do not choose the weights, the vendor chooses them for you, and the machine will then optimise faithfully towards somebody else's priorities for the next ten years. Then hand over to the lab. Tell them they are about to move those weights themselves and watch the recommended operating point slide along the frontier in front of them.

## Slide 76
Lab — SIM-6 · Combustion multi-objective optimiser
Twelve minutes at the keyboard, on the trade-off surface you have just been shown
6. Performance optimisation
76
SIM-6
Combustion multi-objective optimiser
12 minutes at your laptop
Do this
Open SIM-6 and run the optimiser at its default weights. Write down the proposed excess O₂, the burner tilt and the predicted gain in kcal/kWh.
Drag the weight on NOx to maximum and run again. Watch the recommended target slide along the frontier and the heat-rate gain shrink.
Bring the NOx weight back down and settle on a setting you would be willing to defend to your environment cell.
Switch the hard clamps off and re-run. Read what the unconstrained optimiser proposes, and decide whether you would sanction it on a running unit.
Switch the rate limits off and watch the target jump in one step instead of walking there.
Watch for
There is no single best answer — only a frontier, and a choice about where on it you wish to sit.
Weighting NOx heavily is a perfectly legitimate answer. It costs heat rate, and the cost is on the screen in kcal/kWh.
With clamps off, the optimiser asks for an operating point no engineer in this room would sign for.
With rate limits off, the setpoint steps instead of ramping — which is precisely how a boiler gets upset.
Combustion optimisation is a trade-off surface, not a single best answer. Clamps and rate limits are not paperwork — they are the engineering that makes an optimiser safe enough to leave in service.
Notes: [Slide 76 · 6. Performance optimisation · target 15:20] [15:08–15:20] [LAB] Twelve minutes. Get them into SIM-6 quickly and read the five moves aloud before anyone touches a slider. Frame it in one sentence: a response-surface model of a boiler with a weighted-sum optimiser on top of it, running in the browser. Same structure as a real combustion optimiser, smaller. The first two moves are the teaching. When the NOx weight goes to maximum the recommended operating point moves and the heat-rate gain falls. Nothing has broken. The optimiser is doing exactly what it was told. Stop the room after step two and ask somebody to read out both numbers — the NOx figure and the kcal/kWh they gave up to get it. Moves four and five are the safety lesson and they land physically. With clamps removed the optimiser proposes an operating point that is arithmetically optimal and operationally unacceptable. It has no concept of a mill, a burner or a tube. It only has the objective function you gave it. Walk the room. Reconvene at fifteen twenty sharp and ask two people what weights they settled on and why they would defend them.

## Slide 77
Condenser, vacuum and cooling
The cheapest kcal on the station, and the one most often lost quietly
6. Performance optimisation
77
Telling fouling from air ingress
Tube fouling: terminal temperature difference rises while the cooling water temperature rise falls
Air ingress: terminal temperature difference rises with the water side holding, and dissolved oxygen follows
Cleanliness factor computed continuously, not once a year on the day of the performance test
Vacuum pump or ejector duty trended against estimated condenser air load
Ball cleaning judged by the cleanliness factor it delivers, not by the ball counter
Back pressure always read against what is achievable at today's wet bulb
What you can actually change this week
CW pump combination against cooling water inlet temperature and unit load
Cooling tower performance measured as approach to wet bulb, not as outlet temperature
Fill condition, drift and water distribution — the slow losses nobody logs
Tube cleaning scheduled by cleanliness factor rather than by calendar
Air ingress hunted before the planned outage, so the leak is known when the unit opens
Condenser duty checked at part load, where most of the month is actually spent
A 10 mmHg improvement in back pressure is worth an indicative 8 to 12 kcal/kWh on a subcritical unit. Nothing else on the station is that cheap.
Notes: [Slide 77 · 6. Performance optimisation · target 15:32] [15:20–15:22] Two minutes, straight out of the lab and into the most neglected loss on the plant. The left column is a diagnosis that most stations never make. Fouling and air ingress both show as poor vacuum and are treated the same way — with a vacuum complaint in the log. They are different faults with different fixes, and the two of them separate cleanly on terminal temperature difference against cooling water rise. Say that this discrimination needs no new instrument, only the arithmetic done continuously on tags you already historise. The right column is deliberately practical. Point at the wet bulb line. Back pressure judged against a fixed design figure will look bad every May and good every January, and neither reading tells you anything. Judged against what is achievable at today's wet bulb, it tells you whether you have a problem. Ask the room: who computes cleanliness factor more often than once a month? Very few hands. Land the punch. Eight to twelve kcal/kWh for ten millimetres of mercury, indicative, and most of it recoverable with cleaning and a pump schedule rather than capital.

## Slide 78
Auxiliary power is a scheduling problem
81.5 MU above norm in June 2026, worth ₹32.9 crore — all of it consumed inside the fence
6. Performance optimisation
78
Mill combination
Which mills run, at what loading, on which elevations. Habit picks the combination. A search picks a better one, and re-picks it when the load moves.
Fan control mode
Inlet guide vanes against variable speed, and how hard the ID fan is throttling against a damper somebody set years ago and nobody has revisited.
CW pump scheduling
Pump count against cooling water inlet temperature and load. The right number in February is the wrong number in May, and the schedule rarely changes.
ESP field energisation
Fields run at reduced power or de-energised when ash loading genuinely permits, inside the emission limit and continuously verified against opacity.
Compressed air
Leak load, unloaded running hours and receiver pressure. The cheapest auxiliary saving on any station, and by some distance the least glamorous.
Ash handling cycles
Cycle frequency matched to actual ash generation rather than to a fixed timer that was set at commissioning and never questioned since.
Chandrapur 3-7 at 11.69 % against a norm of 8.67 %. Parli 6-7 at 12.41 % against 9.30 %. Nashik at 12.96 % against 10.75 %. None of that is a plant defect.
Notes: [Slide 78 · 6. Performance optimisation · target 15:34] [15:22–15:24] Two minutes. This is the second-largest controllable loss in the company and the one with the least engineering attention on it. Make the framing explicit before the cards: auxiliary power is not principally an efficiency problem, it is a combinatorial scheduling problem. At any load there are many valid combinations of mills, fans, pumps and fields. They are not equally expensive. Operations picks a valid one, because that is the job, and a valid one is not the cheapest one. Read the punch line slowly. Three stations, three gaps of two to three percentage points, sustained over a month. Then say the consequence: 81.5 MU above norm across the fleet in June alone, worth 32.9 crore rupees at each station's own variable charge. That is roughly the annual output of a small unit, consumed behind the gate. Ask the room: at your station, who decides the CW pump combination on a hot afternoon, and against what document? The answer is almost always a person and a habit, not a calculation. Then hand straight over to SIM-3, where they will do that calculation themselves.

## Slide 79
Lab — SIM-3 · Auxiliary power optimiser
Ten minutes at the keyboard, on your own station's typical operating point
6. Performance optimisation
79
SIM-3
Auxiliary power optimiser
10 minutes at your laptop
Do this
Open SIM-3. Set the unit load and the cooling water inlet temperature to the values your own station typically runs at this time of year.
Set the mill, fan, CW pump and ESP configuration you believe your unit is running right now.
Read the configuration the optimiser proposes against the one you entered, and check that every constraint is still satisfied.
Press 'Adopt the optimiser's answer' and read the saving, in MU and in rupees a month.
Raise the cooling water temperature to 38 °C, re-run, and watch the optimum CW pump count change.
Give yourself two minutes to beat the optimiser by hand.
Watch for
The habitual configuration is rarely the cheapest one, and it is never the cheapest one at every load.
The optimum CW pump count moves with cooling water temperature. A February schedule is simply wrong in May.
The saving appears in MU and in rupees at your station's own variable charge, not as a percentage.
Beating a combinatorial search by hand is possible occasionally and impossible consistently.
Auxiliary power is a combinatorial scheduling problem, and a computer solves it better than habit does. The 81.5 MU the fleet burned above norm in June 2026 is largely made of exactly these choices.
Notes: [Slide 79 · 6. Performance optimisation · target 15:36] [15:24–15:34] [LAB] Ten minutes. Insist on step one — their own station's load and cooling water temperature, not the default. The whole value of this module is that the answer is about their unit. Step two matters as much. Make them enter the configuration they think is running right now, from memory. That is the comparison the module exists to make. The teaching moment is step five. Push the cooling water inlet to thirty-eight degrees and the optimum pump count changes. Say aloud what that means: a pump schedule fixed at commissioning is correct on exactly one day of the year, and wrong by some margin on the other three hundred and sixty-four. Step six is deliberately humbling and takes the sting out of the message. Some engineers will match the optimiser once. Nobody matches it repeatedly across load, ambient and equipment availability. That is not a comment on the engineer. It is a comment on how many combinations there are. Walk the room and collect two or three rupee figures. Reconvene at fifteen thirty-four and read the best and the worst aloud.

## Slide 80
How a soft sensor is built
Using the coal GCV estimator as the worked example — the same shape applies to any inferred measurement
6. Performance optimisation
80
BUILD
Laboratory results
the labels — a year of daily samples
Plant signals
mill DP, current, PA flow, feeder, O₂
Time-align
match each lab result to the coal actually fired
Fit a regression
ridge, penalised to resist noise
OPERATE
Hold-out test
on samples never used in training
Report error honestly
RMSE against laboratory scatter
Deploy with limits
flag when inputs fall outside training range
Standing comparison
every new lab result checks the model
Feedback: Retrain on a change of coal source — the single biggest failure mode of a GCV soft sensor
A soft sensor never beats the laboratory it learned from. It interpolates between laboratory results — which is exactly what you need between them.
Notes: [Slide 80 · 6. Performance optimisation · target 15:42] [15:30–15:33] The time-alignment box is the one engineers underestimate. A lab result describes coal sampled at a point in the chain, and the coal actually in the furnace at that moment left the bunker hours earlier. Getting that lag wrong destroys the model, and no algorithm recovers from it. Stress 'Deploy with limits'. When the model is asked about an operating point outside anything in its training set, it will still return a number, confidently. A deployed soft sensor must say 'outside my range' instead. The feedback arrow is the real-world killer. June 2026 shows imported coal at 4,624 to 4,709 kcal/kg blended with domestic at around 3,000. A model trained on one blend will mislead on another. Hand over to SIM-4 if time allows, or point them to it for the evening.

## Slide 81
Soot blowing on demand, not on a timer
The heat transfer surfaces will tell you when they need cleaning — if anyone is listening
6. Performance optimisation
81
1
Estimate effectiveness online
Compute the heat absorbed by each surface — furnace, superheater, reheater, economiser and air heater — from gas and steam side measurements you already historise, every few minutes.
2
Rank the surfaces by need
Compare each surface against its own clean baseline at the same load and coal. The ranking, not the clock, decides which blower operates next.
3
Blow only what is dirty
Sequence the blowers that will genuinely recover heat. Skip the ones that would only consume steam, erode tube surfaces and add to attemperation flow.
4
Verify, then learn
Measure the recovery after each operation. A blower that recovers nothing is telling you about a mechanical defect, not about fouling.
Timer-based blowing wastes steam on clean surfaces and leaves the dirty ones alone. Both cost heat rate, and one of them also costs tube life.
Notes: [Slide 81 · 6. Performance optimisation · target 15:46] [15:34–15:35] One minute. This is a short slide and it should feel like an obvious idea that nobody has implemented. Start with the current practice: soot blowers on a fixed sequence and a fixed interval, because that is what was commissioned. The furnace does not foul on a timetable. It fouls according to coal, load, ash chemistry and how the mills happen to be running. The first step is the one that surprises people, so say it directly: no new instrument is required. Surface effectiveness is computed from gas and steam side temperatures and flows that are already on the DCS. It is arithmetic done continuously, not hardware. Step four is the one to leave them with. If a blower operates and recovers no heat, that is not a fouling result, it is a defect report — a stuck lance, a blocked nozzle or a starved header. The system finds mechanical faults as a by-product of doing its main job. One line to close: less steam consumed, less erosion, cleaner surfaces where it matters. Then move on quickly.

## Slide 82
Coal quality and the GCV soft sensor
As-fired GCV ranges from 2,733 to 3,270 kcal/kg across our own fleet
6. Performance optimisation
82
The gap the laboratory leaves
Bomb calorimeter results arrive hours or days later, on one sample, per rake. The mills are burning something entirely different by the time the figure lands.
What a soft sensor does
Estimates as-fired GCV every few minutes from mill power, air flow, feeder rate, O₂ and steam generation — trained on the laboratory results themselves.
Blend against constraints
Chooses the blend against mill capacity, ESP loading and emission limits, not against price alone. A cheaper coal that de-rates a mill is not cheaper.
Transit-loss analytics
GCV loss between loading and unloading runs 619 to 941 kcal/kg. Rake-level analysis separates sampling error from genuine loss, rake by rake.
Coal is the largest line in the bill, and it is also the one number in the plant that almost nobody knows while it is being burnt.
Notes: [Slide 82 · 6. Performance optimisation · target 15:47] [15:35–15:37] Two minutes. This slide connects the performance block to the fuel bill. Open with the spread. As-fired gross calorific value across our own thirteen groups runs from 2,733 kcal per kilogram at Khaperkheda 5 to 3,270 at Parli 8. That is one company, one procurement function, and a twenty per cent spread in the energy content of the fuel. Explain the soft sensor in plant language: it is not a laboratory replacement, it is a laboratory extension. It learns the relationship between what the boiler is doing and what the laboratory later reports, then predicts the laboratory result continuously. Its error must be reported honestly and it will be, in the lab module. The transit loss card carries the hardest number. Between loading and unloading, GCV falls by 619 to 941 kcal per kilogram. Some of that is sampling method and some of it is real. Nobody currently separates the two, and the separation is worth doing rake by rake before it is argued about in a contract meeting. Ask: at your station, how many hours old is the GCV figure the operator is working to?

## Slide 83
What an advisory looks like at 14:20
A 500 MW unit, the deviation attributed, and a rupee figure attached to the recommendation
6. Performance optimisation
83
Chandrapur Unit 8 · 500 MW · Performance advisory · 14:20
Net heat rate
2,425 kcal/kWh against 2,375 normative — plus 50
Contributor 1 · boiler and turbine
Gross heat rate 2,258 against 2,232 — worth about 27 kcal/kWh
Contributor 2 · auxiliary power
6.90 % against a 6.00 % norm — worth about 23 kcal/kWh
Largest single item
Condenser back pressure above its wet-bulb-corrected expectation — about 11 kcal/kWh
Recommended action
Run condenser ball cleaning this shift; review CW pump count at present cooling water temperature
Value if actioned
About 8 kcal/kWh — roughly ₹27 lakh a month on this unit at its own cost of heat
Advisory means the operator decides. Closed-loop means the system acts within limits you set. Know which one you are buying.
Notes: [Slide 83 · 6. Performance optimisation · target 15:49] [15:37–15:39] Two minutes. This is the whole block on one screen. The top three rows are Chandrapur 8-9's own June 2026 figures: net heat rate 2,425 against 2,375 normative, gross 2,258 against 2,232, auxiliary 6.90 per cent against a 6.00 per cent norm. Do the decomposition aloud — about twenty-seven kcal/kWh of the fifty is boiler and turbine, about twenty-three is auxiliary power. Say clearly that the split below that line is illustrative of how the screen would present it, not an audited attribution. Then walk the structure, because the structure is the lesson. A deviation with both numbers. Contributors ranked, each with kcal/kWh against it. One specific action, not a list. A rupee figure for actioning it — eight kcal/kWh on this unit's June generation at its own cost of heat is about twenty-seven lakh rupees a month. Ask the room whether they would act on this screen. Then read the punch line twice. Advisory and closed-loop are two different purchases with two different safety cases, and vendors routinely blur them in the same presentation.

## Slide 84
Where the money is at your station
Block five close — and the answer is different at every one of the thirteen groups
6. Performance optimisation
84
If auxiliary power is your whole problem
Nashik, Khaperkheda 5, Chandrapur 3-7 and Parli 8 all beat their gross heat-rate norm. Every kcal of their penalty is auxiliary. Start with SIM-3.
If it is boiler and turbine
Koradi 8-10 carries a 176 kcal/kWh gross gap, Paras 3-4 89 kcal/kWh and Koradi 6 56 kcal/kWh. Start with combustion, condenser and air heater.
If it is both
Bhusawal, Khaperkheda 1-4, Chandrapur 8-9 and Parli 6-7 carry both. Do the decomposition first and stop guessing which half is the larger one.
The Monday version
One unit, one month of historian data, one decomposed loss account. No purchase order and no vendor is required to produce that.
₹56 crore of net heat-rate gap and ₹33 crore of excess auxiliary power in a single month. Both are addressable with data this company already owns.
Notes: [Slide 84 · 6. Performance optimisation · target 15:51] [15:39–15:40] One minute, then the break. Do not introduce anything new. The point of this slide is that there is no fleet answer. Read the first two cards against each other. Nashik's gross heat rate is seventeen kcal/kWh better than its normative figure — the boiler and turbine are doing their job and the entire fifty kcal/kWh penalty is auxiliary consumption at 12.96 per cent against a 10.75 per cent norm. Koradi 8-10 is the mirror image, with a 176 kcal/kWh gross gap on nearly 965 MU of generation. Say the consequence: if Nashik buys a combustion optimiser it will have bought the wrong thing, and if Koradi 8-10 starts with pump scheduling it will have started in the wrong place. The decomposition costs nothing and it comes first. End on the Monday card, because it is the only one that requires action from them. One unit, one month, one loss account. Everything in this block was built on exactly that. Give them the exact time to return, and finish early.

## Slide 85
7
SESSION
Generative AI, RAG and agents
Turning thirty years of manuals, SOPs and RCA reports into something you can ask a question
What a language model is, and why it is confident when wrong
The RAG pipeline, end to end, with citations
From assistant to agent — the reason-act-observe loop
Where it will let you down, and what to never use it for
15:55 – 16:28
33 minutes
Hands-on: SIM-7 and SIM-8
85
Notes: [Slide 85 · 7. Generative AI, RAG and agents · target 15:55] [15:55] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 86
What a language model actually is
Next-token prediction — and why it sounds most confident exactly when it is wrong
7. Generative AI, RAG and agents
86
WHAT IT IS — A MODEL OF LANGUAGE
A very good guess at the next word
It was trained on an enormous quantity of text to predict what word comes next. Everything it does — summarising, drafting, explaining, translating between Marathi and English — is that single operation repeated. It has learned the shape of technical writing extremely well.
WHAT IT IS NOT — A SOURCE OF TRUTH
It has no idea what is true
There is no database inside it and no lookup step. A plausible sentence and a correct sentence feel identical to it, so it produces both in the same fluent, confident, well-formatted English. Fluency is not evidence. Confidence is not accuracy.
A brilliant assistant and a terrible authority. Treat every unsourced answer as a draft written by somebody who has never seen your plant.
Notes: [Slide 86 · 7. Generative AI, RAG and agents · target 15:55] [15:50–15:52] Two minutes, and get the mental model right before anything else in this block. Explain next-token prediction with a plant sentence. Start 'the boiler feed pump discharge pressure is' and the model will complete it with something entirely plausible. It is completing a pattern, not consulting a record. Everything else it appears to do is that operation, repeated at scale. Then the honest part, which this audience will respect. There is no database inside it. When it produces a clause number, a setting or a torque value it is completing a pattern that looks like a clause number. Sometimes that pattern happens to be correct. It has no way of knowing which. Ask the room whether anyone has caught one of these tools inventing something. Usually a few hands, usually with a good story. Let one person tell it. Land the punch. Brilliant assistant, terrible authority. The rest of this block is entirely about how to keep the assistant and remove the authority — and the answer is not a better model, it is your own documents.

## Slide 87
The plant knowledge problem
Everything you need to answer a question at two in the morning, and none of it findable
7. Generative AI, RAG and agents
87
OEM manuals
Thousands of pages per package, across several vendors and several decades. Searchable only by whoever remembers which volume it was in.
SOPs and operating instructions
Written, revised, superseded. The current version and three obsolete ones sit in the same folder with almost the same file name.
RCA and trip reports
The most valuable documents on the station. Written once, filed, and almost never read again by anyone outside the original committee.
Defect and work-order history
Years of CMMS free text. Every fault this station has ever had is in there, in a form nobody can count or sort.
Drawings and protection settings
P&IDs, single-line diagrams, relay settings, interlock schemes — the highest-consequence documents, held under the strictest version control.
Tacit knowledge
The engineer who knows why that damper has been at 40 per cent since 2014. That knowledge walks out of the gate on the day he retires.
None of this is a data problem. All of it is a language problem — and language is the one thing this technology is genuinely good at.
Notes: [Slide 87 · 7. Generative AI, RAG and agents · target 15:57] [15:52–15:53] One minute. Move briskly; this slide only has to be recognised, not taught. Read the cards as a description of their own working day rather than as a list. The test question to put to the room: at two in the morning, with a unit tripped, how long does it take to find the current version of the relevant operating instruction and the last time this same trip happened? Nobody says minutes. The RCA card is the one to stop on. Those documents are the most expensive knowledge the station produces — a committee, weeks of work, the truth about a real failure — and they are read once. A failure repeats at another station three years later and nobody knows the report exists. The tacit knowledge card lands by itself in this room. Do not over-explain it. Land the punch. Every item on this slide is text written by engineers for engineers. That is precisely the material this technology handles well, and it is why the generative AI conversation for a power station starts with documents and not with chatbots.

## Slide 88
Three ways to make a model know your plant
Prompting, retrieval and fine-tuning — and only one of them belongs in a power station
7. Generative AI, RAG and agents
88
Approach | What it needs | When knowledge updates | When it is the right choice
Prompting | You paste the relevant text into the question yourself | Only what you pasted, only this time | One-off questions on a document already open in front of you
Retrieval (RAG) | Your documents, indexed and tagged with unit, revision and date | The moment you re-index a revised document | Almost always — this is the answer for a power station
Fine-tuning | Thousands of curated question-and-answer pairs, and GPU time | Never, until you retrain and re-validate the whole model | Almost never — for tone and format, not for facts
Fine-tuning teaches a model how to speak. Retrieval teaches it what is true today. Your revision-control problem is a retrieval problem.
Notes: [Slide 88 · 7. Generative AI, RAG and agents · target 15:58] [15:53–15:55] Two minutes. This is the slide that will save somebody a wasted procurement. Work across the third column, because it decides everything. With prompting, the knowledge lasts one question. With retrieval, a revised SOP is live the moment it is re-indexed. With fine-tuning, the knowledge is baked into the weights and the only way to change it is to retrain and re-validate. Then say the sentence they need to carry into a vendor meeting: a power station's documents change constantly — revisions, circulars, modified settings, new trip reports every month. Any approach that requires retraining to reflect a revision is structurally wrong for us, regardless of how impressive the demonstration was. Be fair to fine-tuning so it does not sound like prejudice. It is genuinely useful for making a model write in a house style or produce a fixed report format. It is not a way to teach it facts that change. Ask whether anyone has been offered a fine-tuned model trained on their manuals. If yes, the follow-up question is: what happens when the manual is revised?

## Slide 89
RAG, explained properly
Search first, then answer — and show the passage the answer came from
7. Generative AI, RAG and agents
89
1
Index your documents
Manuals, SOPs, RCA and trip reports are split into passages. Each passage is tagged with station, unit, document number, revision and effective date, and stored so it can be searched by meaning.
2
Ask in plain language
The engineer types the question the way they would ask a colleague. No document number, no keyword syntax, no need to know which manual holds the answer.
3
Search before answering
The system retrieves the handful of passages most likely to contain the answer, filtered to the station and unit you asked about, and places them in front of the model.
4
Answer from those passages only
The model is instructed to answer from what was retrieved, to cite each source, and to say that it does not know when the passages do not contain the answer.
An answer you cannot trace is an answer you cannot use. The citation is not decoration — it is the entire control.
Notes: [Slide 89 · 7. Generative AI, RAG and agents · target 16:00] [15:55–15:56] One minute, delivered crisply. The four steps are the whole architecture. The order is the point, so say it as a sentence: search first, then answer. A plain chatbot answers from memory. A retrieval system finds the passage first and then writes an answer constrained to it. That single reordering is the difference between a novelty and an engineering tool. Step four contains the instruction that matters most, and it is worth reading aloud: say that you do not know when the passages do not contain the answer. A model that admits ignorance is far more useful than one that always produces something, and that behaviour is configured, not hoped for. Make the honest caveat now rather than later. Retrieval reduces invention sharply. It does not eliminate it, which is why the citation exists — so an engineer can open the source and check in thirty seconds. Land the punch and move straight on. An answer you cannot trace is an answer you cannot use, whatever it says and however well it reads.

## Slide 90
Metadata matters more than the model
The failure is never 'the AI was stupid'. It is 'the AI answered about the wrong unit'.
7. Generative AI, RAG and agents
90
Station and unit on every chunk
Koradi Unit 8 and Koradi Unit 10 are not the same machine. Without a unit tag the retriever cannot tell them apart, and it will not try.
Revision and effective date
A superseded SOP retrieves exactly as well as the current one. Unless the revision is on the passage, the model quotes whichever reads better.
Document class and status
Manual, SOP, trip report, drawing, circular — and current, superseded or withdrawn. A withdrawn procedure must never surface as an answer.
The concrete failure
You ask about the Unit 4 boiler feed pump and receive the Unit 3 answer: correctly cited, fluently written, and completely wrong for your machine.
Ninety per cent of the engineering in a plant retrieval system is metadata and version control. The model is the easy part.
Notes: [Slide 90 · 7. Generative AI, RAG and agents · target 16:01] [15:56–15:57] One minute. This is the slide that separates people who have built one of these from people who have watched a demonstration. Go straight to the fourth card and tell it as an incident, because it is the failure everybody eventually meets. An engineer asks about the Unit 4 boiler feed pump. The system retrieves a passage from the Unit 3 manual, because the two documents read almost identically. It answers fluently and cites its source correctly. Every part of the machinery worked. The answer is wrong for that machine, and the citation makes it look more trustworthy, not less. Say the diagnosis plainly: nothing about the model caused that. It was a missing tag. The revision card is the same failure in a different dress, and it is the one that carries safety weight. A superseded procedure retrieves just as well as the current one unless status is on the passage. Land the punch. When somebody in this company scopes a retrieval project, the effort is in the filing, the tagging and the version control — and that work is done by engineers who know the documents, not by data scientists.

## Slide 91
Lab — SIM-7 · Retrieval over plant documents
Ten minutes at the keyboard, on an indexed corpus of plant documents
7. Generative AI, RAG and agents
91
SIM-7
RAG over plant documents
10 minutes at your laptop
Do this
Open SIM-7 and run the default ID fan question. Before you read the answer, read the retrieved passages and their similarity scores.
Now read the answer and check every sentence of it against the passages it cites.
Switch 'Grounded' off and ask the same question. Compare the invented answer with the cited one, line by line.
Turn hybrid search off and search for a document code. Watch pure meaning-based search fail on an exact string.
Filter by station and unit, then re-run a question that was previously answered from another unit's document.
Watch for
The retrieval step happens first and is completely visible. Nothing is magic once you can read the passages yourself.
Ungrounded, the model writes a confident, plausible, well-structured answer with no source and at least one invention in it.
Meaning-based search alone cannot find an exact document code. Keyword matching is still needed alongside it.
The unit filter is the thing that stops a Unit 3 passage answering a Unit 4 question.
The difference between an ungrounded chatbot answer and a retrieval-grounded answer with citations is not a matter of degree. One can be checked in thirty seconds. The other cannot be checked at all.
Notes: [Slide 91 · 7. Generative AI, RAG and agents · target 16:02] [15:57–16:07] [LAB] Ten minutes. Read the five moves aloud before they start, and insist on the order in step one — passages first, answer second. Frame the module honestly: this is real TF-IDF retrieval with cosine similarity over an indexed plant corpus, running in the browser. The retrieval is genuine. The answer generation is simulated so that the module works offline, and the contrast it demonstrates is exactly the one you meet in a real system. Step three is the moment that lands. Grounded off, the same question produces a fluent, confident, structured answer with no source — and something in it is invented. Stop the room there and ask somebody to read both answers aloud, one after the other. Most people cannot tell which is which from the writing alone. That is the entire lesson. Step four is the practical one engineers appreciate. Meaning-based search is poor at exact strings, which is why real systems run keyword and semantic search together. Walk the room. Reconvene at sixteen zero seven and ask what they had to check in the ungrounded answer to catch the invention.

## Slide 92
The RAG pipeline, end to end
What happens between an engineer's question and a cited answer
7. Generative AI, RAG and agents
92
INDEXING — once per document, then on revision
Documents
manuals, SOPs, RCA and trip reports, SAP text
OCR where needed
scanned drawings and old reports
Chunk
passage-sized pieces that stand alone
Attach metadata
station, unit, document, revision, date
Embed and index
stored in your own system
ANSWERING — every question
Question
"HP heater level high on Unit 4 — what do I check?"
Hybrid search
keyword for tag numbers, semantic for meaning
Filter by metadata
this unit, this station, current revision
Re-rank
best few passages, not the most
Answer with citations
only from those passages
Feedback: A superseded revision must leave the index the day it is superseded — version control is your job, not the model's
The language model appears in exactly one box, at the very end. Everything that determines whether the answer is trustworthy happens before it.
Notes: [Slide 92 · 7. Generative AI, RAG and agents · target 16:10] [16:05–16:09] This is the most important diagram of the afternoon. It is the answer to 'but it makes things up'. Walk the top lane and stop at 'Attach metadata'. This is where the Unit 4 versus Unit 3 failure is prevented, and it is the step every rushed implementation skips. Walk the bottom lane. At 'Hybrid search', explain why pure semantic search fails on tag numbers and equipment codes — the very things engineers actually search for. At 'Answer with citations', make the point that the model is constrained to the retrieved passages and told to say so when they do not contain the answer. The punch line is the takeaway: the language model is one box out of 10. Buying a better model does not fix a bad index. Hand over to SIM-7, where they can watch the retrieval happen before the answer appears.

## Slide 93
Practical uses in our own workflow
Eight things worth trying, none of which touch a control system
7. Generative AI, RAG and agents
93
Shift handover drafting
Drafted from the log, the alarm list and work in progress. The outgoing engineer corrects it and signs it. Ten minutes recovered, every shift.
Trip report first drafts
Sequence of events, protections operated and plant response assembled into a first draft within the hour, while the committee is still being formed.
Troubleshooting assistant
Describe the symptom in plain language and receive the relevant manual sections, past defects and previous RCAs, with citations, in one place.
Precedent search across the fleet
Has this failure happened at another station? Today that question needs a phone call and some luck. It should need a search box.
Work-order text into a taxonomy
Years of free-text CMMS entries classified by equipment, failure mode and cause — turning unreadable text into countable reliability data.
Specification drafting
First-cut technical specifications and tender clauses assembled from your own earlier documents, so house style and referenced standards survive.
Marathi and English safety communication
Toolbox talks, safety circulars and site instructions in both languages, so nothing important is understood only by those who read English.
Summarising inspection reports
Overhaul and inspection reports condensed into findings, actions and open points, with every point traceable to the paragraph it came from.
Every one of these produces a draft for an engineer to check. None of them produces a decision. That distinction is the whole safety case.
Notes: [Slide 93 · 7. Generative AI, RAG and agents · target 16:12] [16:07–16:08] One minute. Do not read all eight — point at three and let them read the rest. Pick the three with the strongest pull for this room. Shift handover, because everybody does it and everybody does it under time pressure. Precedent search across the fleet, because five stations have almost certainly each solved the same failure separately and none of them know it. And the work-order taxonomy, because it is the one that turns text into numbers, and it is the bridge to the next slide. The Marathi and English card deserves a sentence of its own. Safety communication that is only understood by people who read English is not safety communication, and translation is something this technology does genuinely well. Ask the room to pick one card each, silently, that would save them time this week. Then say the constraint out loud, twice if necessary: every one of these produces a draft. An engineer reads it, corrects it and signs it. Nothing here writes to a plant system, nothing here closes a work order, and nothing here decides anything.

## Slide 94
Why we cannot explain 57.85 per cent
Tying language back to the June 2026 numbers
7. Generative AI, RAG and agents
94
THE RELIABILITY QUESTION
Why was availability 57.85 %?
Khaperkheda Units 1-4 ran at 57.85 per cent availability in June 2026 and Chandrapur 3-7 at 64.88 per cent. Between them they carry ₹45.69 crore of the fixed-charge disallowance. Nobody can currently say which failure modes account for how much of it.
WHY WE CANNOT ANSWER IT
The history is free text
Every one of those outages is recorded — in work orders, log books and trip reports, written by different people in different words over many years. You cannot count what has never been classified, and a Pareto chart of unclassified text does not exist.
Structuring that history is a language problem, not a reliability problem. Solve the language problem and the reliability analysis becomes ordinary engineering.
Notes: [Slide 94 · 7. Generative AI, RAG and agents · target 16:13] [16:08–16:09] One minute, and make it the slide that justifies the whole block to a sceptic. State the position without softening it. Khaperkheda 1-4 at 57.85 per cent availability, the lowest in the fleet. Chandrapur 3-7 at 64.88 per cent. Between them, 45.69 crore rupees of the cumulative fixed-charge disallowance — 21.75 and 23.94 respectively. Then ask the question everyone assumes has an answer: what are the top five causes, ranked by hours lost, at Khaperkheda 1-4 over the last three years? Nobody in this company can produce that ranking today. Not because the data is missing — it is all there — but because it is in free text written by dozens of people who each described the same failure differently. Say the reframing clearly, because it is the point of the slide. That is not a reliability engineering problem. It is a text classification problem, and it is exactly what this technology does well. Structure the history and the Pareto chart follows in an afternoon. One line to close: we are not short of failure data. We are short of countable failure data.

## Slide 95
From assistant to agent
A model given tools, a goal, and permission to decide the order of the calls
7. Generative AI, RAG and agents
95
1
Reason
Given a goal — find out why Unit 8 ID fan vibration is rising — the agent decides what it needs to know first and which tool will tell it. That decision is not scripted by anyone.
2
Act
It calls one tool: a historian query, a CMMS lookup, a performance calculation, a document search. One call at a time, and every call is written into a visible trace.
3
Observe
It reads the result and updates its plan. A flat vibration trend sends it somewhere quite different from a rising one. This is where an agent stops resembling a script.
4
Repeat, then stop at the gate
It loops until it has an answer or runs out of steps, then puts its finding, its evidence and its proposed action in front of a human who approves or refuses.
A chatbot answers. A script follows a fixed path. An agent chooses the path — which is precisely why it must stop at a human gate before anything is actioned.
Notes: [Slide 95 · 7. Generative AI, RAG and agents · target 16:14] [16:09–16:10] One minute. Define the word properly, because it is the most abused term in this year's sales material. Use the three-way contrast in the punch line as your structure. A chatbot answers from what it was given. A script follows a path an engineer wrote in advance, and does the same thing every time. An agent is given a goal and a set of tools and works out the order of calls for itself. Make the loop concrete with the case they are about to run. The goal is to find out why Unit 8 ID fan vibration is rising. The agent pulls the trend first, sees it climbing, then looks up the defect history for that fan, then finds the last inspection report. If the trend had been flat, its second call would have been different. Nobody wrote that branch. Then state the consequence honestly. The flexibility that makes an agent useful is the same property that makes its behaviour impossible to fully test in advance. Which is why step four is not a feature to be configured away — it is the reason the thing is deployable at all.

## Slide 96
What a tool is, for a power station
An agent is only as safe as the narrowest tool you hand it
7. Generative AI, RAG and agents
96
Tool | What it does | Access level | Why it is drawn this way
Historian query | Fetches tag trends for a plant item over a stated period | Read-only | No mechanism exists to write anything back to the historian
CMMS lookup | Finds defect history, open work orders and spares for that item | Read-only | Raising or closing a work order stays a human act
Performance calculation | Runs your own heat-rate and loss model on the retrieved data | Compute only | Touches no plant system and holds no plant credentials
Document search | Retrieves manual, SOP and RCA passages with citations | Read-only | The corpus is a copy; the agent cannot alter a document
Read-only is safe. Write-capable — a report generator that files the report, a tool that raises the work order or moves a setpoint — is a permission, not a convenience, and it needs a human at the gate every single time.
Notes: [Slide 96 · 7. Generative AI, RAG and agents · target 16:15] [16:10–16:11] One minute. This is the engineering answer to 'is an agent safe', and it is not about the model at all. Make the principle explicit before the table: the agent's blast radius is defined entirely by the tools you give it, not by how clever or careful it is. A model with four read-only tools cannot do harm to plant no matter what it concludes. The same model with one write-capable tool can. Walk the fourth column, which is the design reasoning. Each tool is deliberately narrow. The historian tool cannot write. The CMMS tool can read defect history but cannot raise or close a work order. The performance tool computes and holds no credentials. Then take the punch line slowly, because it names the fifth tool everybody wants. A report generator that drafts is read-only. A report generator that files the report is write-capable, and that is a different safety case entirely — as is anything that raises a work order or moves a setpoint. One closing line: specify the access level of every tool in the contract, in writing, before the first demonstration impresses anybody.

## Slide 97
Lab — SIM-8 · Agentic work-order assistant
Ten minutes at the keyboard, on the Koradi Unit 8 ID fan scenario
7. Generative AI, RAG and agents
97
SIM-8
Agentic AI work-order assistant
10 minutes at your laptop
Do this
Open SIM-8 and start the Koradi Unit 8 ID fan scenario. Step it forward one tool call at a time — do not press run-all.
At each step read the agent's stated reasoning before you look at what the tool returned, and decide whether you would have made the same call.
Continue to the approval gate. Read the proposed work order, its evidence and its priority, then approve or refuse it yourself.
Tick 'grant write access' and read the warning that appears. Do not skim it.
Re-run with one tool disabled and watch the agent's plan change around the missing information.
Watch for
The plan is not fixed. What the historian returns changes which tool the agent reaches for next.
Every call, every result and every inference is on the screen. An agent whose trace you cannot audit is not deployable.
The approval gate is where engineering judgement lives, and it is the only place it lives.
With write access granted, the same trace that was advice becomes an instruction. The warning is not boilerplate.
An agent is a planner that calls tools. The visible trace is what makes it reviewable and the human approval gate is what makes it deployable. Neither of the two is optional.
Notes: [Slide 97 · 7. Generative AI, RAG and agents · target 16:16] [16:11–16:21] [LAB] Ten minutes, the last lab of the day. Insist on step one — one call at a time, nobody presses run-all. The value is entirely in watching the plan form. Step two is the teaching. Reading the reasoning before the result forces them to judge the agent as they would judge a junior engineer: was that the right thing to look at next? Sometimes it is not, and noticing that is the skill they are meant to leave with. Step three is the one to stop the room on. Make everybody actually decide — approve or refuse — and then ask two people which way they went and why. There is no correct answer. There is only a named engineer who owns the decision, which is the entire point of the gate. Step four should feel uncomfortable and it is meant to. Read the warning aloud once the room has seen it. Granting write access converts an advisory trace into an instruction that reaches a real system, and it is a decision for a committee, not for a checkbox. Reconvene at sixteen twenty-one. Two slides left, and both matter.

## Slide 98
The agent loop
Reason, act, observe, repeat — and where the loop is required to stop
7. Generative AI, RAG and agents
98
THE LOOP — repeats until the agent has enough
Goal
triage this residual advisory
Reason
what do I need to know next?
Choose a tool
historian, CMMS, documents, calculation
Act
the call is made with read-only credentials
THE STOP
Observe
what came back, and does it fit?
Enough?
if not, loop back and ask the next question
Draft the output
work order, advisory note, report
HUMAN APPROVAL GATE
a named engineer signs, or does not
Feedback: Every loop iteration and every tool call is logged, so the reasoning can be reconstructed afterwards
The loop is what makes it an agent. The gate is what makes it acceptable in a power station.
Notes: [Slide 98 · 7. Generative AI, RAG and agents · target 16:21] [16:16–16:19] Contrast this with a script. A script has a fixed sequence somebody wrote. An agent decides its next call based on what the last one returned — that is the entire difference, and it is what makes it useful for triage, where you cannot know in advance which question matters. Point at 'Act' and note the words 'read-only credentials'. Every tool in the loop reads. Nothing in the loop writes. Point at the gate. Say plainly: 'This box is not a formality and it is not removable. The agent can compress half a day of investigation into ninety seconds and lay out its evidence. It does not make the decision.' The logging arrow matters for a public-sector utility — if an action is questioned six months later, every step is reconstructable. Hand over to SIM-8, which is this diagram executed one step at a time.

## Slide 99
Where it will let you down
Five failure modes, every one of them seen in practice, none of them fixed by a better model
7. Generative AI, RAG and agents
99
Confident and wrong
It will invent a clause number, a setting or a torque value in fluent English and cite nothing at all. Grounding and citations reduce this sharply. Nothing eliminates it.
Version and unit drift
A superseded SOP or another unit's manual retrieves just as well as the correct one. Without revision and unit metadata you get correct answers to the wrong question.
It cannot do sums
A language model predicts text, not arithmetic. Any heat rate, efficiency or rupee figure must be produced by a calculation tool and checked — never lifted from the prose.
Prompt injection
Text inside an ingested document can carry instructions the model will follow. A scanned circular is not a trusted input, and an agent with write access makes that dangerous.
Confidentiality
Plant drawings, protection settings, tender papers and commercial data leaving the company through a public service is a breach, whatever the privacy statement claims.
Never use a language model for: protection settings · clearance and permit decisions · safety-critical procedure changes · statutory returns without verification · anything reaching the plant without an engineer's signature
Notes: [Slide 99 · 7. Generative AI, RAG and agents · target 16:26] [16:21–16:23] Two minutes, and read the band at the bottom slowly. This is the slide that decides whether the room trusts everything else in the block. Take the arithmetic card seriously, because it surprises people who assume a computer can add. The model predicts text. A heat rate that looks right and is wrong by forty kcal/kWh reads exactly like a heat rate that is correct. Any number must come from a calculation tool and be checked by an engineer. Prompt injection needs the concrete version. Someone scans a circular. Inside it is a line of text addressed to the model rather than to a reader. The model follows it, because it cannot distinguish an instruction from content. Harmless in an advisory system, serious in an agent with write access — which is another argument for the gate. The confidentiality card is a policy point, not a technical one. Protection settings and tender documents pasted into a public service have left the company, and no privacy statement changes that. Read the never line aloud, word by word. Nothing in this course goes near a protection setting or a permit decision. Nothing reaches the plant without an engineer's signature.

## Slide 100
What to try on your own documents
Block six close — four things that need no purchase order
7. Generative AI, RAG and agents
100
Pick one corpus, not all of them
One package's manuals, its SOPs and its last five RCAs. Small, current and version-controlled. A corpus you can trust beats a large one you cannot.
Fix the metadata before the model
Station, unit, document number, revision, effective date, status. Tag fifty documents by hand and you will learn more than from any vendor demonstration.
Test with questions you already know
Ask twenty questions whose answers you know, from your own documents. Count how many come back cited and correct. That number is your business case.
Structure one year of work orders
Take one unit's CMMS free text and classify it by failure mode. The Pareto chart at the end is the one nobody in this company currently has.
Retrieval over your own documents is the cheapest, safest and fastest-returning AI project available to this company — and it begins with a filing exercise, not a model.
Notes: [Slide 100 · 7. Generative AI, RAG and agents · target 16:28] [16:23–16:25] Two minutes to close the block. Nothing new, and finish on time. Take the four cards as instructions rather than suggestions. The first one prevents the commonest failure, which is starting with every document the station owns and producing a system nobody trusts. One package, current documents, version controlled. The second card is the honest one. The work is filing and tagging, and it is done by engineers who know which document supersedes which. Say clearly that this is not a data science task and never has been. The third card is the one to press hardest, because it is how they hold a vendor to account. Twenty questions with known answers, from their own documents. Count how many come back correctly cited. That count is the acceptance test, and it costs nothing to run. The fourth card connects back to the availability numbers. One unit, one year of work orders, classified. The output is a ranked list of what actually stops your machines — and Khaperkheda 1-4 at 57.85 per cent availability is waiting for exactly that list. Then hand over for the closing session.

## Slide 101
8
SESSION
Computer vision and emerging applications
Thermal, CCTV, drones and acoustics — and an honest maturity rating for everything else
Vision in the plant, from switchgear to conveyor belts
What a vision model needs from you
Acoustic and ultrasonic methods
Proven, Emerging, Experimental — and how to tell
16:28 – 16:40
12 minutes
101
Notes: [Slide 101 · 8. Vision and emerging · target 16:28] [16:28] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 102
Computer vision in the plant
Six places a camera earns its keep — and one boundary that decides whether the programme survives
8. Vision and emerging
102
Thermal on electrical plant
Switchgear, busduct joints, cable terminations and transformer bushings. A loose or degrading connection appears as heat long before it fails.
Thermal on boiler and coal
Casing and duct insulation loss, refractory condition, air preheater hot spots, and spontaneous combustion developing inside the coal stockpile.
Conveyors and CHP
Belt tear and misalignment, chute spillage, idler condition and foreign objects — the failures that stop coal reaching the bunkers.
Leak detection
Steam and oil leaks picked up on camera, including areas people rarely walk: roof levels, bunker floors and duct runs behind plant.
Drones and crawlers
Chimney and flue liner, cooling tower shell, ash dyke survey, and stockpile volume by photogrammetry. Subject to DGCA permissions.
Safety and zones
Restricted-area intrusion, hot-work monitoring and man-down detection. Monitor zones and equipment — never individual behaviour.
Monitor zones and equipment, not individuals. Behaviour monitoring raises privacy and industrial-relations issues that will sink the programme before it delivers anything.
Notes: [Slide 102 · 8. Vision and emerging · target 16:28] [16:25–16:28] Three minutes, six cards, and one boundary that decides whether the programme lives. Move quickly through the first five. Thermal on electrical plant is the easiest win in this block — a loose busduct joint shows as heat weeks before it fails, and most stations already own a thermal camera and use it once a quarter. Fixed thermal on the same assets, trended, is a different proposition altogether. Coal stockpile spontaneous combustion deserves a sentence: thermal sees a hot spot developing inside the pile before anyone smells it. Conveyors and CHP are where the money sits at most stations, because a belt tear stops coal to the bunkers and everything downstream follows. On drones, say the DGCA point plainly, because somebody will ask. Permissions are a real constraint, not a formality. Then stop on card six and say it slowly. Monitor zones and equipment. Do not monitor individual behaviour. The moment a camera project is seen as watching workers rather than watching plant, it acquires a privacy and industrial-relations problem that will sink it, and rightly so.

## Slide 103
What a vision model actually needs from you
The unglamorous work that decides whether a camera project delivers or embarrasses you
8. Vision and emerging
103
What the model needs
Labelled images — several hundred to a few thousand, marked by somebody who knows the plant
Examples of the fault, not only of normal — and faults are rare by definition
Camera placement fixed, framed on the asset, and not moved after training
Lighting that is consistent, or a thermal camera that does not care about light
Lens cleaning, condensation and coal dust treated as a maintenance task with an owner
A named engineer to review and correct wrong detections weekly for the first few months
What people get wrong
Assuming a model bought for another station will work here — it will not
Different camera, angle, lighting or equipment means re-labelling, not reconfiguration
Expecting the demonstration accuracy on your own dusty, back-lit, monsoon images
Installing cameras first and deciding what to detect afterwards
No plan for who acts on a detection at two in the morning
Treating labelling as a one-off, when the plant and the model both keep changing
A model trained at one station will not transfer to another without re-labelling. Transfer learning shortens that work; it does not remove it.
Notes: [Slide 103 · 8. Vision and emerging · target 16:31] [16:28–16:30] Two minutes. This is the reality check that keeps them out of a bad procurement. Say the headline first: a vision model is not clever software you install. It is a model somebody trained on labelled pictures of your plant, and the labelling is the project. Work down the left column briefly. Several hundred to a few thousand labelled images, marked by somebody who knows what a healthy idler looks like. Examples of the fault, which are rare by definition. A camera that stays exactly where it was when the images were taken. Consistent lighting, or thermal instead of lighting. And somebody whose job includes cleaning the lens. The right column is what goes wrong in procurement. Land the transfer point hard, because it decides the fleet strategy. A model trained at one station will not work at the next without re-labelling — different camera, different angle, different lighting, different equipment. Ask the room who has been shown a demonstration claiming ninety-nine per cent accuracy. Then ask on whose images it was measured. The answer is never yours.

## Slide 104
Acoustic and ultrasonic
Listening to the plant — the oldest diagnostic sense, now instrumented and trended
8. Vision and emerging
104
Boiler tube leak detection
Acoustic emission sensors on the waterwall and second pass hear a leak as rising high-frequency energy, often days before the unit trips.
Cross-check with a mass balance
Pair the acoustic signal with a data-driven makeup water mass balance. Two independent indications turn a suspicion into a defensible outage decision.
Steam and air leak surveys
Ultrasonic detectors find compressed air and steam leaks that a walkdown misses. Auxiliary power and heat-rate loss, both directly costed.
Acoustic pyrometry
Time-of-flight of sound across the furnace builds a temperature map where no thermocouple survives. Useful for combustion and burner balancing.
The acoustic signal tells you something is leaking. The mass balance tells you how much. Neither on its own justifies pulling a unit off bars.
Notes: [Slide 104 · 8. Vision and emerging · target 16:33] [16:30–16:33] Three minutes on the sense we use least and should use most. Boiler tube leak detection by acoustic emission is the strongest item in this block. Sensors on the waterwall and the second pass hear a leak as a rise in high-frequency energy, often days before the unit trips. That is the difference between a planned shutdown and a forced outage, and forced outages are what produced the hundred crore rupees of fixed-charge disallowance we looked at this afternoon. Card two is the engineering discipline. An acoustic signal on its own moves people to argue. Pair it with a data-driven makeup water mass balance and you have two independent indications pointing the same way. That combination justifies a decision to pull a unit; neither alone does. Steam and air leak surveys with ultrasonic detectors are cheap and unglamorous. Compressed air leaks are pure auxiliary power, and they sit inside the auxiliary number from session four. Acoustic pyrometry is the interesting one — sound across the furnace where no thermocouple survives. Flag it as emerging, and tell them we rate it honestly on the next slide.

## Slide 105
Emerging applications, honestly rated
A filter to apply to every vendor presentation you attend for the next two years
8. Vision and emerging
105
Acoustic boiler tube leak detection
Acoustic emission sensors alarmed on rate of change, confirmed against a makeup water mass balance
Proven — with a mass-balance cross-check
Thermal and CCTV analytics
Fixed cameras and detection models on electrical plant, conveyors, leaks and restricted zones
Proven for thermal · Emerging for video
Drone and crawler inspection
Aerial and crawling platforms carrying camera and thermal payloads where people cannot safely go
Proven — subject to DGCA permissions
Acoustic pyrometry
Time-of-flight of sound across the furnace reconstructs a temperature map for combustion balancing
Emerging — few installations in India
Digital twin
A calibrated hybrid of physics and data, kept live and honest against the running unit
Emerging — heavy engineering to sustain
Agentic assistants
A planner that calls historian, CMMS and performance tools, with a human approval gate
Experimental — approval gate not optional
Reinforcement learning for unit control
An agent learning a control policy by trial, which means learning from failures you cannot allow
Experimental — not on a live unit
Buy Proven. Pilot Emerging. Read about Experimental — and be suspicious of anyone selling it to you today.
Notes: [Slide 105 · 8. Vision and emerging · target 16:36] [16:33–16:36] Three minutes, and this is the slide they should photograph. Tell them what the table is for: it is a filter to apply to every vendor presentation they will attend for the next two years. Read the right-hand column before the left. The top three can be bought today with a straight face. Acoustic tube-leak detection with a mass-balance cross-check. Thermal analytics on electrical plant. Drone and crawler inspection, subject to DGCA permissions. Note carefully that thermal is proven while general video analytics is younger — the distinction matters when a vendor sells both on one slide. The middle two are pilots. Acoustic pyrometry has few installations in India. The digital twin is a genuine idea — a calibrated hybrid of physics and data kept live against the running unit — but it is the engineering effort to sustain it that people underestimate. The bottom two: agentic assistants are experimental and the human approval gate is not optional. Reinforcement learning for unit control learns by making mistakes, and a live unit is not a place where mistakes are permitted. Land the punch and pause on the last clause.

## Slide 106
Block close — vision and emerging
Four things to carry into the last session of the day
8. Vision and emerging
106
Cameras are cheap; labels are not
The cost of a vision project sits in labelling, mounting, lighting and weekly correction of wrong detections. It does not sit in the model.
Nothing transfers for free
A model trained at one station needs re-labelling at the next. Budget for it, or the second site will fail and the programme will be cancelled.
Zones and equipment, never people
Individual behaviour monitoring will end the programme. Keep the scope on plant condition and on restricted areas, and say so in writing.
Two defensible starts
Fixed thermal on electrical plant, and acoustic tube-leak detection cross-checked against a makeup water mass balance. Both produce a number an engineer can check.
Buy Proven. Pilot Emerging. Read about Experimental — and ask any vendor which one they are selling.
Notes: [Slide 106 · 8. Vision and emerging · target 16:39] [16:36–16:38] Two minutes to close the block. Do not add new material. Card one is the cost correction. Every station in this room can afford cameras. What they must budget for is labelling, mounting, lighting, cleaning and a weekly review of wrong detections through the first months. That is where vision projects die, and it never appears on the quotation. Card two repeats the transfer point deliberately. If the company decides to roll something out to a second station, budget for re-labelling. A programme that assumes free replication will fail at site two, and site two failing is what gets the whole thing stopped. Card three is non-negotiable and worth saying aloud one more time: zones and equipment, never individuals. Card four gives them something to do rather than something to admire. If a station wants to start with this block, there are two defensible starts, both with clear failure modes and both producing a number an engineer can verify by walking to the plant. Then hand over: everything today only works if it is implemented responsibly, and that is the last twenty minutes.

## Slide 107
9
SESSION
Implementing AI responsibly
Data quality, the safety boundary, governance — and choosing one pilot you can actually finish
Three rules: data quality, the safety and cyber boundary, human in the loop
Governance for a state utility
Why programmes fail, and sizing the prize honestly
One pilot per station, from your own June 2026 evidence
16:40 – 17:00
20 minutes
107
Notes: [Slide 107 · 9. Implementing responsibly · target 16:40] [16:40] Section divider. Say the session title, name the two or three things they will be able to do at the end of it, and if there is a lab in this session, say so now so laptops are open. Ten to fifteen seconds — do not talk over a divider.

## Slide 108
Rule one — data quality and engineering validation
Before the algorithm, the tag list. This is the least glamorous slide of the day and the most important.
9. Implementing responsibly
108
What will bite you
Historian compression and exception deviation quietly discarding the excursion you needed
Frozen transmitters reading a flat, plausible value for months on end
Calibration drift learned by the model as normal behaviour
An asset hierarchy that does not match between DCS, historian and SAP
Tags that exist in the DCS but were never historised at all
Timestamp misalignment between systems, so cause appears to arrive after effect
What good practice looks like
Audit the tag list before the first model, not after the first failure
Check compression settings on every tag the model will actually use
Validate every model output against first-principles engineering
Reconcile the asset hierarchy once, properly, across DCS, historian and SAP
Keep a named owner for the tag list — a person, not a department
Treat data quality as permanent maintenance, not a project phase
Most plant AI projects fail on the asset hierarchy, not on the algorithm.
Notes: [Slide 108 · 9. Implementing responsibly · target 16:40] [16:38–16:41] Three minutes. This is rule one, so say why it comes first. Left column, and be concrete. Historian compression is the one nobody expects: compression and exception deviation settings are chosen to save disk, and they discard precisely the small excursions a model needs. A frozen transmitter reads a flat, plausible number for months and every model downstream believes it. Calibration drift gets learned as normal. And timestamps that differ between DCS and historian will show cause arriving after effect, which no algorithm can repair. Right column is what a competent station does. Audit the tag list before the first model. Validate every output against first-principles engineering — if the model says the condenser is fouling, the terminal temperature difference should agree. Name an owner for the tag list, because a department is not an owner. Then land the punch and mean it. Most plant AI projects fail on the asset hierarchy, not on the mathematics. Three systems, three different names for the same pump, and nobody authorised to reconcile them. Ask the room directly: does your station have one agreed asset hierarchy today?

## Slide 109
Rule two — the safety and cyber boundary
Where AI may go, where it may go only with engineering controls, and where it must never go
9. Implementing responsibly
109
NEVER
Protection systems, trip logic, interlocks and any safety instrumented function. No model, no advisory, no exception, at any station.
WITH CONTROLS
Closed-loop optimisation writing biases to the DCS — with clamps, rate limits, a watchdog, bumpless transfer, operator override and documented approval.
FREELY
Advisory systems, anomaly alerts, performance advisories, decision support and knowledge assistants. Validate the output; the engineer still decides.
Segmentation
Purdue levels with IEC 62443 zones and conduits, drawn and agreed on paper. The historian sits in the demilitarised zone. Nothing on the plant network talks directly to a corporate or cloud analytics service.
Read-only by default
Every AI system starts with read access to process data and nothing else at all. Write access back to the DCS is a separate, engineered, approved decision — never a setting somebody quietly changes.
One-way data paths
Where data must cross from OT to IT, use a unidirectional gateway or a data diode. Physics enforces the direction of flow, not a firewall rule that can be edited.
OEM remote access
The single largest OT risk at most stations, and usually nobody's job to manage. It must be time-boxed to the visit, logged, supervised by a station engineer, and disabled by default between sessions.
AI-specific risks
Four risks that are genuinely new: plant data leaving the fence, model poisoning through corrupted history, prompt injection hidden inside a document the assistant reads, and supply-chain risk in machine-learning packages.
Notes: [Slide 109 · 9. Implementing responsibly · target 16:43] [16:41–16:44] Three minutes, and this is the most important slide in the deck. Slow down and read the red layer aloud exactly as written. Protection systems, trip logic, interlocks and any safety instrumented function. No model, no advisory, no exception. If a vendor proposes anything that touches these, the conversation is over. The amber layer is where closed-loop optimisation lives. It is legitimate, but only with clamps on the bias, rate limits on how fast it may move, a watchdog that returns control on loss of signal, bumpless transfer, an operator override on the panel and a documented approval. Say clearly that the clamps are the engineering — the model is the easy part. The green layer is where every station in this room should start. Advisories, anomaly alerts, performance advisories, knowledge assistants. Validate them, then let the engineer decide. On cyber, spend your remaining time on OEM remote access. At most stations it is the largest single OT risk and it belongs to nobody. Finish on the AI-specific card. Prompt injection hidden inside a document an assistant reads is new, and most of this room has not heard of it.

## Slide 110
Rule three — human in the loop
The system advises, the engineer decides. Both halves of that sentence have to stay true in practice.
9. Implementing responsibly
110
Trust calibration
Two failures. Under-trust, where nobody opens the alerts and the system quietly dies. Over-trust, where the operator stops thinking. The second is far more dangerous.
Alert fatigue
Twenty alerts in the first fortnight and the system is finished. Start with three machines, tune persistence, and earn the right to add more.
Workflow fit
If the output does not arrive in the shift log, the round sheet or the work order, it does not exist. A separate screen is a screen nobody opens.
Accountability
The decision stays with the named engineer. Record what the system said, what the engineer decided, and why — especially when the two differ.
Under-trust is visible and recoverable. Over-trust is invisible until the day the model is wrong — and that is the day it matters.
Notes: [Slide 110 · 9. Implementing responsibly · target 16:46] [16:44–16:46] Two minutes on the human side, and it matters more than it looks. Card one is the heart of it. There are two ways trust fails. Under-trust is when nobody opens the alerts and the system quietly dies — embarrassing, visible, and recoverable. Over-trust is when the operator stops thinking because the screen is usually right. Say plainly which is more dangerous: the second, because the failure stays invisible until the day the model is wrong. Alert fatigue is how most systems are killed in the first fortnight. Twenty alerts, three of them useful, and the credibility is spent. Trust is spent once. Workflow fit gets designed last and should be designed first. If the output does not appear where the engineer already works, it does not exist. Accountability closes it. The engineer decides. Record what the system said, what the engineer decided and why — particularly when the two differ, because that record is what protects the engineer afterwards. Ask the room: who here has stopped reading an alarm list because it cried wolf? Every hand goes up.

## Slide 111
Governance for a state utility
What has to exist on paper before a fleet programme — not after the first audit query
9. Implementing responsibly
111
An AI usage policy
One page, circulated. Permitted uses, prohibited uses, and who approves an exception. A forty-page policy is a policy nobody reads.
Data classification
What is public, internal, confidential and regulated — and an explicit list of what may never be pasted into a public AI service.
Verification requirement
Any AI-produced figure that leaves the station is checked by a named engineer against source data before it reaches a report or a filing.
Record keeping and audit trail
Prompts, outputs, model versions and approvals retained. If a decision is questioned two years later, the trail has to exist.
DPDP Act 2023
Where personal data is involved — CCTV, biometrics, employee records — consent, purpose limitation and retention are legal obligations, not preferences.
Procurement questions
Where does our data go, who owns the model, what is the accuracy on our plant, what happens at contract end, and who sustains it.
Notes: [Slide 111 · 9. Implementing responsibly · target 16:48] [16:46–16:48] Two minutes. This is the slide the station head and the IT head need, so tell them to photograph it. The usage policy should be one page. Permitted uses, prohibited uses, and who approves an exception. Data classification is the practical one. Everybody in this room has a phone with a public AI assistant on it. The organisation has to say explicitly what may never be pasted into it — tender documents, protection settings, personnel records, anything commercially confidential. If nobody says it, people will guess, and they will guess generously. Verification is the discipline that keeps all of this defensible. Any AI-produced figure that leaves the station is checked by a named engineer against source data before it reaches a report or a regulatory filing. Record keeping matters more in a state utility than in a private one, because decisions are examined years later. The DPDP Act applies wherever personal data is involved. That is a legal obligation, not a preference. Read the six procurement questions aloud. They are worth more in a vendor meeting than any technical evaluation form.

## Slide 112
What happens after go-live
The lifecycle nobody budgets for, and the reason models quietly stop working
9. Implementing responsibly
112
WATCHING
Model in service
producing advisories daily
Monitor the inputs
has a tag frozen, drifted or been rescaled?
Monitor the residuals
is the model's own error growing?
Monitor the actions
is anyone acting on the alerts?
RENEWING
Trigger
drift, an overhaul, a retrofit, new coal
Curate the window
an engineer selects genuinely healthy history
Retrain and validate
prove it still catches known past events
Approve and redeploy
versioned, dated, with a named owner
Feedback: Put 'retrain the models' in the outage checklist, next to 'recalibrate the instruments'
A model is a piece of plant. It degrades, it needs overhauling, and it needs an owner. Budget for it or lose it.
Notes: [Slide 112 · 9. Implementing responsibly · target 16:48] [16:46–16:49] This is where programmes die, eighteen months after the launch photograph. The fourth box of the top lane is the one nobody instruments: is anyone acting on the alerts? Usage telemetry — how many alerts were opened, how many led to an action — tells you whether the system is alive long before the benefit numbers do. The feedback arrow is the single most actionable line on the slide. Adding 'retrain the affected models' to the outage checklist costs nothing and prevents the most common post-overhaul failure, where the machine is now a different machine and the model has not been told. End on the punch. Treat the model like plant. It has an owner, a maintenance interval and a failure mode. Anything else and it becomes shelfware with a licence fee attached.

## Slide 113
Why AI programmes fail
Eight failures seen again and again, and the countermeasure for each one
9. Implementing responsibly
113
WHY IT FAILED
WHAT PREVENTS IT
Started with technology, not a problem
Write the problem and its rupee value before any vendor call
Bought a platform, not an outcome
Contract on a validated result at one unit, not on a licence
Pilot ran on and on with no decision
Fix the go or no-go date and the decision-maker up front
No baseline, so the benefit was disputed
Agree the baseline and how it is calculated on day one
Operators heard about it after go-live
Shift engineers in the design review from week one
Data promised by IT, never delivered
Extract and inspect 12 months of history before signing
Scaled to the fleet before proving one unit
One machine, one owner, one proven result, then replicate
Nobody budgeted to run it after year one
Fund support, retraining and tags in the same sanction
Every one of these is an organisational failure, not a technical one — which is good news, because you control all of them.
Notes: [Slide 113 · 9. Implementing responsibly · target 16:50] [16:48–16:51] Three minutes, and lead with the punch rather than saving it. Not one of these eight is a mathematics problem. Every one is organisational, and every one sits inside the control of the people in this room. That is genuinely good news and it should be said that way. Row one is the most common. A programme that starts with 'we should do something with AI' has no way of knowing whether it succeeded. Write the problem and its rupee value first — and after this afternoon, every station here can. Row three kills more programmes than any technical fault. A pilot with no decision date runs until the sponsor changes and then quietly stops. Fix the date and name the person who decides. Row four turns a success into an argument. If the baseline is agreed after the result is known, finance will not accept the benefit, and they will be right to refuse. Row seven is the temptation immediately after a good pilot. One machine, one owner, one proven result, then replicate. Ask each station to pick the row most likely to happen to them.

## Slide 114
Sizing the prize honestly
The June 2026 evidence, converted into a first-year target that finance will accept
9. Implementing responsibly
114
Evidence, June 2026 | Value at stake | Where it comes from | Realisation | First-year target
Net heat-rate gap vs MERC norm | ₹56.35 cr/month | 13 thermal groups | 15–25 % | ₹8.5–14.1 cr/mth
— of which auxiliary power | ₹32.91 cr/month | 81.5 MU above norm | 15–25 % | ₹4.9–8.2 cr/mth
Availability disallowance | ₹100.87 cr cumulative | ₹32.93 cr in the June bill | 15–25 % | ₹15.1–25.2 cr
Heat rate, annualised | ≈ ₹676 cr/year | If June is a typical month | 15–25 % | ₹101–169 cr/yr
₹101–169 cr
a defensible first-year heat-rate target at 15 to 25 per cent realisation of the June 2026 gap
Indicative basis
Values are the full gap against MERC normative performance for June 2026. No programme closes a gap entirely — apply a realisation assumption before putting any of this in a business case.
These are the values of closing the gap entirely. No programme does that, and a business case built on full closure will not survive the finance department.
Notes: [Slide 114 · 9. Implementing responsibly · target 16:53] [16:51–16:53] Two minutes, and this slide is what keeps the business case honest. Start with the evidence, which they have already seen this afternoon. Fifty-six point three five crore rupees a month is the net heat-rate gap across the thirteen thermal groups. Thirty-two point nine crore of auxiliary excess is a component of that gap, not an addition to it — say this twice, because adding the two is the most common error in presentations of this kind and finance will spot it immediately. One hundred point eight seven crore is the cumulative fixed-charge disallowance for availability shortfall, of which thirty-two point nine three crore was adjusted in the June bill. Then take the honest step. Apply a realisation assumption of fifteen to twenty-five per cent. That gives roughly eight and a half to fourteen crore a month on heat rate, and roughly one hundred to one hundred and seventy crore across a year if June is a typical month. Land the punch without softening it. These figures are the value of closing the gap entirely. No programme does that, and no credible one claims to.

## Slide 115
Choosing your first pilot
Seven criteria, six candidates, and a ninety-day plan with a name against each phase
9. Implementing responsibly
115
Data already historised
Problem clearly defined
Value at stake is material
Benefit is measurable
Named owner at the station
Result can be deployed
Low acceptance risk
Candidate pilot | Value | Risk | Verdict
BFP or ID fan anomaly detection | High | Low | Strongest first choice — data exists, no process risk
Mill health and choking prediction | High | Low | Close second — mills hurt availability and heat rate together
Auxiliary power optimisation | High | Low | Benefit visible on the meter, so nobody argues about it
Condenser performance and cleaning schedule | Medium | Low | Good second wave — needs sound vacuum instrumentation
Document assistant on SOPs and RCA reports | Medium | Low | No process risk at all — can run alongside the main pilot
Closed-loop combustion optimisation | High | High | Do this third or fourth. Never first.
A 90-day starter plan
Days 1–30
Audit the tag list. Pick one machine. Extract twelve months of history and inspect it properly. Name the owner before anything else starts.
Performance plus C&I Engineer
Days 31–60
Build and validate on history. Confirm the model would have caught known past events, and confirm it stays quiet through normal operation.
Performance Engineer with analytics support
Days 61–90
Run live in shadow mode. Triage every alert, record what was found, and report the benefit against the agreed baseline.
Maintenance Planner with station sponsor
Notes: [Slide 115 · 9. Implementing responsibly · target 16:55] [16:53–16:56] Three minutes. This is the slide that turns a training day into a project. Read the seven criteria across the top quickly, then say which matters most: data already historised. Everything else can be arranged. Twelve months of history cannot be created retrospectively. Work down the candidates. Boiler feed pump or ID fan anomaly detection is the strongest first choice for almost every station here — high value, low risk, no process interference, and the data already exists. Mill health is a close second, because mills hurt availability and heat rate at the same time. Auxiliary power optimisation has one great advantage: the benefit shows on the meter, so nobody argues about the measurement. The document assistant carries no process risk at all, so it can run in parallel with the main pilot. Then be blunt about the last row. Closed-loop combustion optimisation is high value and high risk. It is a station's third or fourth project, never its first, and a vendor proposing it as a first project is telling you something about themselves. Walk the ninety-day plan and stress the named owner in each phase.

## Slide 116
One pilot per station, from your own evidence
Four stations, four different diagnoses, four different first projects — all from June 2026
9. Implementing responsibly
116
Station | The evidence, June 2026 | The pilot | Monday morning
Nashik 3-5 | Aux 12.96 % vs 10.75 %; gross HR 18 kcal/kWh better than norm | Auxiliary power optimisation — the whole 50 kcal/kWh penalty is auxiliary | List the CW pump, mill and ESP field combinations actually run last month
Koradi 8-10 | Gross HR 2,272 vs 2,096 — a 176 kcal/kWh gap on 964.80 MU | Boiler and turbine heat rate: combustion and condenser analytics | Pull a month of O₂, back pressure and unburnt carbon at unit level
Khaperkheda 1-4 | Availability 57.85 %, the fleet's lowest; ₹21.75 cr disallowance | Predictive maintenance on the two machines that forced the outages | List every forced outage of the last 24 months by equipment
Chandrapur 3-7 | Aux 11.69 % vs 8.67 %; secondary oil 3.23 ml/kWh vs 1.00 | Auxiliary power, plus flame stability to avoid oil support | Get oil consumption split by unit and by start-up from the log
Four stations, four different problems, four different first pilots. There is no fleet-wide answer, and anyone selling one has not read your numbers.
Notes: [Slide 116 · 9. Implementing responsibly · target 16:58] [16:56–16:58] Two minutes. Four stations, four different answers, every one from their own June 2026 figures. Nashik first, because it is the cleanest illustration in the fleet. The gross heat rate is seventeen kilocalories per kilowatt hour better than normative. The boiler and turbine are performing well. The entire fifty kilocalorie net penalty is auxiliary consumption at twelve point nine six per cent against a norm of ten point seven five. A combustion optimisation project at Nashik would be effort in the wrong place. Koradi 8-10 is the opposite case. A one hundred and seventy-six kilocalorie gross gap on nine hundred and sixty-five million units. That is a boiler and turbine problem, and it is the largest single item in the fleet. Khaperkheda 1-4 is availability — fifty-seven point eight five per cent, and twenty-one point seven five crore rupees of disallowance. That is a predictive maintenance problem. Chandrapur 3-7 is auxiliary power at eleven point six nine against eight point six seven, with secondary oil at three point two three millilitres per kilowatt hour against a norm of one. Say it plainly: there is no fleet-wide first pilot.

## Slide 117
What to do on Monday morning
Six actions that are free, take under an hour, and need nobody's approval
9. Implementing responsibly
117
Ask how many tags are historised
Call your C&I team with two questions: how many tags are historised, and at what compression and exception deviation setting.
Pick one machine that hurt you twice
One machine that has forced an outage twice in two years. Not a system, not a fleet. One machine, with a name and a number.
Check the history actually exists
Find out whether twelve months of clean history exists for that machine. If it does not, that is your first project.
Ask who would own an alert
If an alert arrived at two in the morning tomorrow, who opens it, who inspects, who closes it? No name means no programme yet.
Put your own numbers in the value table
Your station's PLF, heat rate, as-fired GCV and coal cost into the value table from the handout. The answer then belongs to you.
Run SIM-2 on your own station
Open the simulation lab, select your station, and see for yourself whether your gap is auxiliary power or boiler and turbine.
None of these six needs a sanction, a vendor or a budget. They need one hour and one engineer who decides to ask.
Notes: [Slide 117 · 9. Implementing responsibly · target 17:00] [16:58–17:00] Two minutes to close, and finish on time. Say the framing sentence first: every one of these six is free, takes under an hour, and needs nobody's approval. Card one is the most useful telephone call any of them will make this week. How many tags are historised, and at what compression and exception deviation setting? Most engineers have never asked, and the answer is often uncomfortable. Card two is the question from ten o'clock this morning: one machine that has hurt you twice in two years. Card three follows directly. Does twelve months of clean history exist for it? If not, that is the project, and it is a C and I project rather than an AI project. Card four is the honest test of readiness. If an alert arrived at two in the morning, who opens it? If there is no name, there is no programme yet. Card five makes the economics theirs rather than mine. Card six sends them back to the lab with the file they now own. Thank them, and stop.

## Slide 118
PREDICT · DIAGNOSE · OPTIMISE · ASSIST
Four things AI does well in a power station — and one thing only you can do
What you can do on Monday morning
1
Ask your C&I team how many tags on your unit are actually historised, and at what compression setting
2
Pick one machine that has hurt you twice in the last two years
3
Find out whether twelve months of clean history exists for it
4
Ask who at your station would own an alert if one arrived tomorrow morning
5
Put your own PLF, heat rate, GCV and coal cost into the value table and see what 10 kcal/kWh is worth to you
6
Open the simulation lab and run SIM-2 on your own station's row
The mathematics is the easy part. The data, the ownership and the follow-through are the job.
Questions — including from Koradi, Khaperkheda, Bhusawal and Paras
Notes: [Slide 118 · Close · target 16:57] [16:57–17:00] Close on the four verbs — they are the spine of the day. Run through the six Monday actions. Every one is free, takes under an hour, and requires no approval from anybody. That is deliberate: the worst outcome of a full day like this is that everyone agrees it was interesting and nothing happens. Remind them what they are taking away: this deck, the course material with the full handout and the lab guide, and the simulation lab file itself, which runs offline and can be re-run on their own station's data. Final line, delivered plainly: 'The mathematics is the easy part. The data, the ownership and the follow-through are the job.' Thank the online stations by name — Koradi, Khaperkheda, Bhusawal, Paras — and open the floor. The FAQ section of the course material covers the twelve questions this audience most often asks.